## Slide 1
WELCOME
TO THE OCTOBER EDITION
OF THE 2019
M&R SEMINAR SERIES

## Slide 2: BEFORE WE BEGIN
SAFETY PRECAUTIONS
  PLEASE FOLLOW EXIT SIGN IN CASE OF EMERGENCY EVACUATION
  AUTOMATED EXTERNAL DEFIBRILLATOR (AED) LOCATED OUTSIDE
PLEASE SILENCE CELL PHONES OR SMART PHONES
QUESTION AND ANSWER SESSION WILL FOLLOW PRESENTATION
PLEASE FILL EVALUATION FORM
SEMINAR SLIDES WILL BE POSTED ON MWRD WEBSITE (https://mwrd.org/seminars)
STREAM VIDEO WILL BE AVAILABLE ON MWRD WEBSITE (https://mwrd.org/seminars - after authorization for release is arranged)

## Slide 3: Paul D. O’Brien, P.E.
Mr. Paul D. O’Brien is a Principal Civil Engineer with the Metropolitan Water Reclamation District of Greater Chicago. Working in the Plant Design Management section of the Engineering Department, he is project manager for the design and construction of new sludge thickening facilities and the replacement of Imhoff tanks with primary clarifiers at the Stickney Water Reclamation Plant, a 1440 MGD facility located in suburban Chicago. Prior to these projects, he was in the Construction Division, working as a Resident Engineer at the District’s three largest plants.
Paul has been with the District for twenty-five years. He has a Bachelor of Science from Purdue University, and is a member of the Water Environment Federation, the Illinois Water Environment Association, and the American Nuclear Society. He is a licensed Professional Engineer registered in Illinois and Wisconsin.

## Slide 4: Let the Water Flow: Startup of the New Aerated Grit Facility and Primary Settling Tanks at MWRDGC’s Stickney WRP
Paul O’Brien, PE (MWRDGC)
Notes: Thanks, everyone. For those of you who attended WEFTEC last month, this will be a familiar topic. Ryan Christopher of G&H and I presented this. But for you, you will get the live, extended version, with a drum solo in the middle. I’m sure Tom and Ginger will forgive me.

## Slide 5: Agenda
Overview of Stickney Water Reclamation Plant
Imhoff Tank Replacement Project
Demolition and Construction
Startup
Startup Challenges
Conclusion

## Slide 6: Overview of Stickney WRP
Stickney WRP
  1,440 MGD
  West Side Plant
    Preliminary treatment
    Primary treatment
    Peak capacity of 720 mgd
  Southwest Plant
    Preliminary, primary, secondary treatment
    Over 1,000 mgd preliminary peak capacity
Notes: You all know these figures and could probably recite them in your sleep.

## Slide 7: Overview of Stickney WRP

## Slide 8: West Side Sewage Treatment Works, 1938
Notes: Aerial from 1938

## Slide 9: Imhoff Replacement Project
Imhoff and Skimming Tanks are at the end of useful life
Insufficient ability to isolate processes leading to shutdowns for normal maintenance
Green House Gas (CH4) Emissions from Imhoff Tanks
Odors from Imhoff Tanks
Solids are digested within the lower compartment of the Imhoff tanks, so sludge produces minimal methane within the digesters

## Slide 10: Westside Plant - 2009

## Slide 11: Imhoff Tanks

## Slide 12: Original Imhoff Replacement Projects
4 Projects
  Phase 1 – Contract 08-171-3P
    Work Performed to Isolate Risks
    Demo Imhoff Tanks Battery A
    Site preparation and demo of skimming tanks 1-8
  Phase 2 & 3 – Contract 04-128-3P
    New Aerated Grit Facility (AGF)
    New Primary Settling Tank’s (PST) 1-9
    New TAPS A & B Buildings
    Primary Switchgear Building
  Phase 4
    Demo Imhoff Tanks Battery B
    New Primary Settling Tank’s (PST) 10-18
    New TAPS C Buildings
$41.6M
$224M
$160M

## Slide 13: Hydraulic stress test 480 MGD was determined to be the max we could pass through 8 skimming tanks and 2 Imhoff batteries

## Slide 14: Contract 08-171-3P
Construction Completed 2013
Work Included:
  Skimming Tanks 1-8 and Imhoff Battery A demolished
  Abatement of hazardous material
  145,000,000 gal of sludge removal from Battery A
  Replace Electrical Feeds to Imhoff Batteries B and C
  Site preparation for future contracts

## Slide 15: Contract 08-171-3P

## Slide 16: Contract 08-171-3P

## Slide 17: WS Plant After Imhoff Replacement Project

## Slide 18: Re-evaluation and Incorporating Lessons Learned. --Calumet PSTs were started while 08-171-3P was underway --CWRP AGRT was larger than necessary and maintenance intensive --Calumet PSTs proved more effective at removing solids than anticipated

## Slide 19: WS Plant After Imhoff Replacement Project

## Slide 20: WS Plant After Imhoff Replacement Project

## Slide 21: Aerated Grit Facility – Original Design

## Slide 22: Contract 04-128-3P – Aerated Grit Facility--As-Built

## Slide 23: Contract 04-128-3P
Aerated Grit Facility
  6 Aerated Grit Tanks
9 160’ Diameter PSTs
  System for flow to bypass PSTs and send to secondary process
Tunnel Access Pump Stations (TAPS) A and B
Odor control system for AGF and PSTs

## Slide 24: Contract 04-128-3P
Project Bid
  Summer 2014
  $224 million
  1200 calendar days to construct
Construction
  Notice to Proceed – December 2014
  Startup – November 2018

## Slide 25: Contract 04-128-3P Construction - AGF

## Slide 26: Contract 04-128-3P Construction - AGF

## Slide 27: Contract 04-128-3P Construction - PST

## Slide 28: Contract 04-128-3P Construction - PST

## Slide 29: Contract 04-128-3P Construction - PST

## Slide 30: Contract 04-128-3P Construction – Effluent Conduits

## Slide 31: Contract 04-128-3P Construction - AGF

## Slide 32: Contract 04-128-3P Construction - AGF

## Slide 33: Contract 04-128-3P Construction - PST

## Slide 34: Contract 04-128-3P Construction - PST

## Slide 35: Contract 04-128-3P Startup
Coordination and planning between departments at MWRDGC and contractor
Start up at one third of its maximum design capacity
Limit the flow to give MWRDGC staff time to:
  Adapt and gain experience to new facilities and equipment
  Make necessary adjustments prior to full flow going through the new Project
  Allow sufficient time for the other processes at Stickney to adjust, specifically anaerobic digesters

## Slide 36: Contract 04-128-3P Startup
AGT No. 2
AGT No. 3
AGT No. 4
AGT No. 5
AGT No. 6
AGT No. 7
PST 1B
PST 3B
PST 5B
PST 2A
PST 4A
PST 6A
PST 1A
PST 3A
PST 5A

## Slide 37: Contract 04-128-3P Startup
PST 1B
PST 3B
PST 5B
PST 2A
PST 4A
PST 6A
PST 1A
PST 3A
PST 5A
AGT No. 2
AGT No. 3
AGT No. 4
AGT No. 5
AGT No. 6
AGT No. 7

## Slide 38: Contract 04-128-3P Startup
AGT No. 2
AGT No. 3
AGT No. 4
AGT No. 5
AGT No. 6
AGT No. 7
PST 1B
PST 3B
PST 5B
PST 2A
PST 4A
PST 6A
PST 1A
PST 3A
PST 5A

## Slide 39: Contract 04-128-3P Startup

## Slide 40: Contract 04-128-3P Startup
Official Startup - November 27, 2018
Start of 7-day startup test and 60-day performance test

## Slide 41: Contract 04-128-3P Startup Challenges

## Slide 42: Sludge Vent Containment Structure

## Slide 43: Contract 04-128-3P Startup Challenges

## Slide 44: Chain must be kept in tension

## Slide 45: Contract 04-128-3P Startup Challenges

## Slide 46: Watch for hydraulic surprises!

## Slide 47: Water is not compressible. Air is.

## Slide 48: Contract 04-128-3P Startup Challenges

## Slide 49: Contract 04-128-3P Startup Challenges

## Slide 50: Other Problems
Notes: Gas piping replacement project. Note also that we will either have to continue to feed Imhoff for the foreseeable future or stop completely, as the bugs within the Imhoff tanks will die if not provided with food. R&D says one month is the most we can go w/o sending sewage to IBAT B&C.

## Slide 51: Other Lessons Learned
Provide more flushing valves for lines prone to clogging. Locate valves in accessible areas
Provide more sampling locations for sludge and primary effluent
Coordinate bridge location with scum beach
Increase slope of gravity scum lines
DCS monitoring of current draw for grit screws and tank drives

## Slide 52: Conclusion
Coordination and planning required
Make necessary adjustments and gain experience prior to full flow going through the new Project
Allow sufficient time for the other processes at Stickney to adjust, specifically anaerobic digesters

## Slide 53: Thank you!
Thanks also to:
Ryan Christopher and the design team at Greeley & Hansen
Beth Zerfas and Greg Florek and their staff in the Construction Division