## Lemont Outfall 2021
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2021-01-01 | 2.22 | 7.2 | 3.6 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 437.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-02 | 2.78 | 7.3 | 3.6 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 695.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-03 | 2.69 | 7.2 | 3.6 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 617.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-04 | 2.42 | 7.2 | 4.4 | 3 | 2 | <5 | <4 | <4 | T/X | T/X | T/X | T/X | T/X | T/X | 0.009 | T/X | 543.91 | 0.7 | 3800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-01-05 | 2.41 | 7.3 | 3.6 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 419.96 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.009 | 0.09 | 0.05 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 93.51 | 34.63 | 376 | 0.6 | N/S
2021-01-06 | 2.27 | 7.3 | 4 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 380.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-07 | 2.16 | 7.2 | 3.9 | 8 | 5 | N/S | 5 | 4 | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 350.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-08 | 2.16 | 7.2 | 3.9 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 393.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-09 | 2.07 | 7.2 | 4.2 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 406.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-10 | 2.14 | 7.2 | 4 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 386.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-11 | 2.08 | 7.2 | 4.7 | 6 | 6 | <5 | 8 | 7 | T/X | T/X | T/X | T/X | T/X | T/X | <0.005 | T/X | 325.68 | 0.9 | 36000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-01-12 | 1.92 | 7.2 | 4.7 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 267.89 | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.021 | 0.08 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 79.85 | 29.26 | 320 | 1.1 | N/S
2021-01-13 | 1.91 | 7.4 | 4 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 291.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-14 | 1.33 | 7.2 | 4.2 | T/X | T/X | N/S | 10 | 8 | T/X | T/X | T/X | T/X | T/X | T/X | N/S | <5 | 358.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-15 | 2.44 | 7.2 | 3.9 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 444.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-16 | 2.79 | 7.2 | 3.7 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 490.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-17 | 2.41 | 7.2 | 3.7 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 581.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-18 | 2.43 | 7.2 | 4.1 | 6 | 3 | <5 | <4 | <4 | T/X | T/X | T/X | T/X | T/X | T/X | 0.009 | <5 | 569.22 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-19 | 2.38 | 7.2 | 4.4 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 475.87 | N/S | 10000 | <0.002 | 0.043 | <0.002 | <0.004 | 0.009 | 0.08 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | <3 | 96.55 | 34.91 | 385 | 1 | N/S
2021-01-20 | 2.14 | 7.4 | 4.3 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 440.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-21 | 2.03 | 7.3 | 4.3 | 9 | 4 | N/S | 6 | 4 | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 432.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-22 | 2.08 | 7.4 | 4.2 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 461.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-23 | 1.99 | 7.2 | 7 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 405.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-24 | 2.05 | 7.3 | 7.1 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | 314.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-25 | 1.94 | 7.2 | 6.4 | T/X | T/X | <5 | 13 | 10 | 1002 | 168 | T/X | <0.3 | 22.68 | T/X | <0.005 | <5 | 257.54 | 0.9 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-01-26 | 1.99 | 7.4 | 7.3 | T/X | T/X | N/S | 12 | 10 | 1234 | 86 | T/X | <0.3 | 23.27 | T/X | N/S | N/S | 427.73 | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.018 | 0.12 | N/S | <0.002 | 0.01 | 0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 86.71 | 32.13 | 349 | 1.2 | N/S
2021-01-27 | 1.9 | 7.4 | 7.6 | T/X | T/X | N/S | 16 | 14 | 1630 | 204 | T/X | <0.3 | 23.84 | T/X | N/S | N/S | 557.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-28 | 1.85 | 7.4 | 7 | 15 | 6 | N/S | 13 | 11 | 1290 | 190 | T/X | <0.3 | 24.25 | T/X | N/S | N/S | 428.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-29 | 1.83 | 7.3 | 7.6 | N/S | N/S | N/S | 17 | 7 | 1160 | 164 | T/X | <0.3 | 23.93 | T/X | N/S | N/S | 339.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-30 | 1.93 | 7.3 | 7.6 | N/S | N/S | N/S | 5 | 4 | 1066 | 132 | T/X | <0.3 | 23.45 | T/X | N/S | N/S | 304.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-31 | 2.38 | 7.3 | 8 | T/X | T/X | N/S | 14 | 11 | 1556 | 150 | T/X | <0.3 | 23.07 | T/X | N/S | N/S | 593.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-01 | 2.11 | 7.2 | 6.3 | T/X | T/X | <5 | 6 | 6 | 1982 | 138 | T/X | <0.3 | 21.2 | T/X | 0.009 | 7 | 871.16 | 0.9 | 5000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-02-02 | 2.08 | 7.2 | 7.2 | T/X | T/X | N/S | 37 | 32 | 1882 | 152 | T/X | <0.3 | 20.58 | T/X | N/S | N/S | 807.48 | N/S | N/S | <0.002 | 0.049 | <0.002 | <0.004 | 0.017 | 0.16 | 0.06 | <0.002 | 0.027 | <0.002 | <0.004 | <0.004 | 0.043 | <0.002 | <0.002 | <0.002 | N/S | 98.9 | 34.98 | 391 | 1.5 | N/S
2021-02-03 | 2.07 | 7.4 | 7.4 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | <0.3 | 21.35 | T/X | N/S | N/S | 647.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-04 | 2.06 | 7.3 | 7.3 | T/X | T/X | N/S | 22 | 22 | 1528 | 202 | T/X | <0.3 | 21.61 | T/X | N/S | N/S | 592.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-05 | 2.18 | 7.3 | 7 | N/S | N/S | N/S | 17 | 15 | 1888 | 132 | T/X | <0.3 | 20.92 | T/X | N/S | N/S | 810.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-06 | 2.09 | 7.4 | 8.2 | N/S | N/S | N/S | 18 | 15 | 1636 | 134 | T/X | <0.3 | 21.03 | T/X | N/S | N/S | 728.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-07 | 2.17 | 7.1 | 6.9 | T/X | T/X | N/S | 22 | 18 | 1328 | 136 | T/X | <0.3 | 20.73 | T/X | N/S | N/S | 471.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-08 | 2.15 | 7.2 | 7.9 | 18 | 7 | <5 | 13 | 11 | 1168 | 136 | T/X | <0.3 | 20.54 | T/X | <0.005 | <5 | 406.67 | 1 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-02-09 | 2.05 | 7.2 | 7.8 | T/X | T/X | N/S | 9 | 8 | 1184 | 150 | T/X | 0.4 | 21.32 | T/X | N/S | N/S | 455.68 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.016 | 0.1 | N/S | <0.002 | 0.017 | <0.002 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | N/S | 86.24 | 30.6 | 341 | 1.2 | N/S
2021-02-10 | 2.07 | 7.3 | 8.2 | 16 | 9 | N/S | 9 | 10 | 1196 | 130 | T/X | 0.6 | 22.2 | T/X | N/S | N/S | 459.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-11 | 2.06 | T/X | 8.2 | T/X | T/X | N/S | 4 | 5 | 1162 | 146 | T/X | T/X | T/X | T/X | N/S | N/S | 256.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-12 | 1.99 | T/X | 7.1 | N/S | N/S | N/S | 8 | 7 | 1142 | 156 | T/X | T/X | T/X | T/X | N/S | N/S | 345.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-13 | 2.01 | T/X | 6 | N/S | N/S | N/S | 6 | 7 | 1122 | 154 | T/X | T/X | T/X | T/X | N/S | N/S | 330.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-14 | 2.03 | T/X | 5.2 | T/X | T/X | N/S | 8 | 8 | 1122 | 138 | T/X | T/X | T/X | T/X | N/S | N/S | 334.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-15 | 2.02 | T/X | 6.2 | T/X | 16 | <5 | 10 | 10 | 1106 | 150 | T/X | 1.1 | 23.48 | T/X | <0.005 | 5 | 327.61 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-16 | 2 | T/X | 6 | T/X | T/X | N/S | 38 | 35 | 1180 | 188 | T/X | 1.2 | 22.77 | T/X | N/S | N/S | 354.55 | N/S | 210000 | <0.002 | 0.04 | <0.002 | <0.004 | 0.026 | 0.18 | N/S | <0.002 | 0.023 | <0.002 | <0.004 | <0.004 | 0.066 | <0.002 | <0.002 | <0.002 | T/X | 88.33 | 31.49 | 350 | 2.3 | N/S
2021-02-17 | 1.98 | T/X | 8.5 | T/X | T/X | N/S | 27 | 23 | T/X | T/X | T/X | 1.1 | 22.59 | T/X | N/S | N/S | 398.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-18 | 1.99 | T/X | 6.5 | T/X | 14 | N/S | 8 | 7 | 1230 | 156 | T/X | 0.9 | 20.96 | T/X | N/S | N/S | 404.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-19 | 1.99 | T/X | 7 | N/S | N/S | N/S | 10 | 8 | 1216 | 156 | T/X | 0.6 | 20.27 | T/X | N/S | N/S | 422.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-20 | 2.01 | T/X | 6.9 | N/S | N/S | N/S | T/X | T/X | 1192 | 158 | T/X | 0.9 | 20.57 | T/X | N/S | N/S | 382.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-21 | 2.08 | T/X | 6.2 | T/X | T/X | N/S | 10 | 9 | 1160 | 166 | T/X | 1.6 | 18.99 | T/X | N/S | N/S | 359.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-22 | 2.45 | T/X | 6.4 | 16 | 10 | <5 | 13 | 12 | 2064 | 176 | T/X | 1.5 | 17.04 | T/X | <0.005 | <5 | 947.05 | 0.9 | 3800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-02-23 | 3.32 | T/X | 6.9 | N/S | N/S | N/S | 7 | 6 | 2584 | 232 | N/S | 1.8 | 14.15 | N/S | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.059 | <0.002 | <0.004 | 0.014 | 0.09 | N/S | <0.002 | 0.024 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 106.04 | 35.97 | 413 | 1.8 | N/S
2021-02-24 | 4.21 | T/X | 2.7 | N/S | N/S | N/S | 5 | 6 | 2548 | 262 | N/S | 1.1 | 9.76 | N/S | N/S | N/S | 1263.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-25 | 4.2 | 7.4 | 6.5 | 10 | 6 | N/S | 10 | 10 | 2260 | 296 | T/X | 0.4 | 10.22 | T/X | N/S | N/S | 1075.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-26 | 4.11 | 7.2 | 6.4 | N/S | N/S | N/S | 6 | 5 | 1992 | 254 | T/X | 1.9 | 9.5 | T/X | N/S | N/S | 922.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-27 | 3.22 | 7.3 | 6.6 | N/S | N/S | N/S | 5 | 4 | 1738 | 202 | T/X | 1.6 | 9.61 | T/X | N/S | N/S | 773.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-28 | 4.13 | 7.2 | 7 | T/X | T/X | N/S | 4 | <4 | 1474 | 196 | T/X | <0.3 | 9.5 | T/X | N/S | N/S | 635.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-01 | 4.2 | 7.2 | 6.8 | T/X | T/X | <5 | 4 | <4 | 1212 | 170 | T/X | 0.6 | 8.89 | T/X | <0.005 | <5 | 509.83 | 0.4 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-03-02 | 4.2 | 7.4 | 7.3 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 2.5 | N/S
2021-03-03 | 4.2 | 7.2 | 7 | T/X | T/X | N/S | 10 | 9 | 1322 | 152 | T/X | 1.6 | 9.37 | T/X | N/S | N/S | 528.03 | N/S | N/S | <0.002 | 0.048 | <0.002 | <0.004 | 0.015 | 0.13 | N/S | <0.002 | 0.017 | 0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 98.34 | 36.55 | 396 | N/S | N/S
2021-03-04 | 4.13 | 7.2 | 6.2 | 5 | 3 | N/S | 6 | 4 | 1290 | 148 | T/X | 2.2 | 9.41 | T/X | N/S | N/S | 517.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-05 | 4.03 | 7.3 | 6.8 | N/S | N/S | N/S | 11 | 9 | 1392 | 174 | T/X | 2 | 10.34 | T/X | N/S | N/S | 550.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-06 | 3.38 | 7.2 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1430 | 202 | T/X | 1.3 | 11.24 | T/X | N/S | N/S | 560.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-07 | 4.01 | 7.2 | 6.8 | T/X | T/X | N/S | 6 | 5 | 1350 | 196 | T/X | 1.7 | 12.55 | T/X | N/S | N/S | 498.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-08 | 3.95 | 7.3 | 6.6 | 9 | 3 | T/X | 4 | <4 | 1220 | 122 | T/X | 2.5 | 12.1 | T/X | T/X | <5 | 479.63 | 0.7 | 910 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S
2021-03-09 | 2.69 | 7.2 | 7 | T/X | T/X | <5 | 6 | 6 | 1190 | 122 | T/X | 0.7 | 13.65 | T/X | 0.011 | N/S | 417.62 | N/S | 2200 | <0.002 | 0.046 | <0.002 | <0.004 | 0.013 | 0.08 | 0.05 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | <3 | 95.73 | 35.91 | 387 | 1.3 | N/S
2021-03-10 | 2.88 | 7.2 | 6.1 | T/X | T/X | N/S | 5 | 4 | 1148 | 174 | T/X | 0.8 | 14.93 | T/X | N/S | N/S | 391.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-11 | 3.06 | 7.4 | 6 | 7 | 5 | N/S | 5 | 5 | 1208 | 164 | T/X | 2.5 | 15.39 | T/X | N/S | N/S | 403.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-12 | 2.56 | 7.3 | 5.8 | N/S | N/S | N/S | <4 | <4 | 1222 | 174 | T/X | 1.7 | 16.79 | T/X | N/S | N/S | 408.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-13 | 2.45 | 7.3 | 7.4 | N/S | N/S | N/S | 4 | 4 | 1176 | 168 | T/X | 0.4 | 19.33 | T/X | N/S | N/S | 368.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-14 | 2.3 | 7.2 | 6.9 | T/X | T/X | N/S | 4 | 4 | 1204 | 168 | T/X | 0.6 | 20.59 | T/X | N/S | N/S | 385.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-15 | 2.47 | 7.3 | 6.1 | 12 | 5 | <5 | 6 | 5 | 1154 | 116 | T/X | 1 | 20.61 | T/X | <0.005 | <5 | 397.28 | 0.9 | 87000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-03-16 | 2.49 | 7.4 | 6.5 | T/X | T/X | N/S | 6 | <4 | 1368 | 166 | T/X | 0.4 | 18.97 | T/X | N/S | N/S | 502.93 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.008 | 0.06 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | 78.75 | 28.67 | 315 | 1.1 | N/S
2021-03-17 | 2.85 | 7.3 | 6.1 | T/X | T/X | N/S | 4 | <4 | 1362 | 138 | T/X | 0.3 | 17.25 | T/X | N/S | N/S | 530.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-18 | 4.2 | 7.3 | 7.1 | 10 | 3 | N/S | 5 | <4 | 1160 | 132 | T/X | <0.3 | 11.89 | T/X | N/S | N/S | 465.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-19 | 4.2 | 7.2 | 6.3 | N/S | N/S | N/S | 12 | 8 | 1174 | 140 | T/X | <0.3 | 11.19 | T/X | N/S | N/S | 438.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-20 | 4.2 | 7.2 | 5.8 | N/S | N/S | N/S | 8 | 7 | 1106 | 130 | T/X | 0.7 | 11.68 | T/X | N/S | N/S | 389.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-21 | 2.99 | 7.2 | 7.2 | T/X | T/X | N/S | 4 | <4 | 1160 | 150 | T/X | 1 | 13.37 | T/X | N/S | N/S | 396.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-22 | 3.24 | 7.4 | 7.8 | 20 | 7 | <5 | 14 | 11 | 1216 | 150 | T/X | 1.7 | 15.27 | T/X | 0.01 | <5 | 407.33 | 0.8 | 29000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-03-23 | 2.37 | 7.4 | 6.1 | T/X | T/X | N/S | <4 | <4 | 1176 | 156 | T/X | 0.4 | 17 | T/X | N/S | N/S | 397.78 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.007 | 0.06 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 88.54 | 33.96 | 361 | 1 | N/S
2021-03-24 | 2.76 | 7.3 | 5.8 | T/X | T/X | N/S | 7 | 5 | 1146 | 130 | T/X | 0.7 | 17.72 | T/X | N/S | N/S | 407.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-25 | 2.75 | 7.2 | 5.5 | T/X | T/X | N/S | <4 | <4 | 1160 | 188 | T/X | 0.6 | 18.21 | T/X | N/S | N/S | 399.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-26 | 3 | 7.3 | 6 | N/S | N/S | N/S | <4 | <4 | 1124 | 180 | T/X | 0.7 | 16.77 | T/X | N/S | N/S | 390.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-27 | 2.65 | 7.3 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1104 | 164 | T/X | 0.4 | 16.82 | T/X | N/S | N/S | 371.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-28 | 2.44 | 7.4 | 7.1 | T/X | T/X | N/S | <4 | <4 | 1070 | 170 | T/X | <0.3 | 17.95 | T/X | N/S | N/S | 335 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-29 | 2.36 | 7.3 | 6.9 | 3 | <2 | <5 | <4 | <4 | 1028 | 184 | T/X | <0.3 | 18.26 | T/X | <0.005 | <5 | 304.75 | 0.8 | 9000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S
2021-03-30 | 2.26 | 7.5 | 6.5 | T/X | T/X | N/S | 7 | 6 | 984 | 124 | T/X | <0.3 | 18.13 | T/X | N/S | N/S | 288.36 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | N/S | 90.26 | 34.85 | 369 | 0.8 | N/S
2021-03-31 | 2.15 | 7.5 | 6.5 | T/X | T/X | N/S | 4 | <4 | 1014 | 166 | T/X | <0.3 | 18.43 | T/X | N/S | N/S | 287.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-01 | 2.12 | 7.4 | 7.5 | 15 | 5 | N/S | 10 | 8 | 1016 | 160 | T/X | <0.3 | 19.23 | T/X | N/S | N/S | 272.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-04-02 | 2.1 | 7.5 | 7.2 | N/S | N/S | N/S | 18 | 14 | 998 | 184 | T/X | <0.3 | 19.75 | T/X | N/S | N/S | 255.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-03 | 2.15 | 7.4 | 7.6 | N/S | N/S | N/S | 5 | 5 | 972 | 134 | T/X | <0.3 | 18.95 | T/X | N/S | N/S | 247.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-04 | 2.21 | 7.4 | 6.4 | T/X | T/X | N/S | 5 | 4 | 938 | 172 | T/X | <0.3 | 18.65 | T/X | N/S | N/S | 239.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-05 | 2.19 | 7.4 | 6.4 | 9 | 3 | <5 | 5 | 4 | 954 | 176 | T/X | <0.3 | 16.57 | T/X | <0.005 | <5 | 236.85 | 0.9 | 5700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-04-06 | 2.09 | 7.4 | 5.4 | T/X | T/X | N/S | <4 | <4 | 952 | 176 | T/X | <0.3 | 15.44 | T/X | N/S | N/S | 236.23 | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.008 | 0.05 | 0.04 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 92.3 | 34.68 | 373 | T/X | N/S
2021-04-07 | 2.07 | 7.4 | 6 | T/X | T/X | N/S | <4 | <4 | 958 | 140 | T/X | <0.3 | 17.73 | T/X | N/S | N/S | 242.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-08 | 2.09 | 7.4 | 5.5 | 3 | <2 | N/S | <4 | <4 | 964 | 176 | T/X | <0.3 | 18.06 | T/X | N/S | N/S | 249.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-09 | 2.49 | 7.3 | 6.4 | N/S | N/S | N/S | <4 | <4 | 1032 | 168 | T/X | <0.3 | 16.75 | T/X | N/S | N/S | 310.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-10 | 2.51 | 7.3 | 6.3 | N/S | N/S | N/S | <4 | <4 | 976 | 176 | T/X | <0.3 | 16.58 | T/X | N/S | N/S | 286.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-11 | 2.5 | 7.3 | 6.1 | T/X | T/X | N/S | 5 | 5 | 960 | 114 | T/X | <0.3 | 15.56 | T/X | N/S | N/S | 284.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-12 | 2.47 | 7.3 | 5.6 | 5 | <2 | T/X | <4 | <4 | 968 | 186 | T/X | <0.3 | 16.16 | T/X | <0.005 | <5 | 290.66 | 0.8 | 4700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-04-13 | 2.39 | 7.3 | 6.8 | T/X | T/X | N/S | 7 | 5 | 982 | 190 | T/X | <0.3 | 16.79 | T/X | N/S | N/S | 266.15 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.006 | 0.08 | N/S | <0.002 | 0.024 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 84.43 | 33.2 | 348 | 1 | N/S
2021-04-14 | 2.09 | 7.4 | 5.9 | T/X | T/X | N/S | 6 | 6 | 950 | 164 | T/X | 0.4 | 17.3 | T/X | N/S | N/S | 243.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-15 | 2.1 | 7.3 | 5.9 | 16 | 5 | N/S | 9 | 7 | 958 | 156 | T/X | 0.5 | 19.54 | T/X | N/S | N/S | 241.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-16 | 2.12 | 7.3 | 6 | N/S | N/S | N/S | 5 | 4 | 980 | 154 | T/X | 0.5 | 18.92 | T/X | N/S | N/S | 225.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-17 | 2.09 | 7.4 | 6.5 | N/S | N/S | N/S | 9 | 7 | 956 | 134 | T/X | 0.3 | 19.67 | T/X | N/S | N/S | 221.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-18 | 2.11 | 7.4 | 6.9 | T/X | T/X | N/S | 11 | 10 | 934 | 144 | T/X | 0.6 | 18.75 | T/X | N/S | N/S | 243.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-19 | 2.15 | 7.4 | 5.5 | 20 | 5 | <5 | 15 | 13 | 962 | 126 | T/X | 0.3 | 16.86 | T/X | 0.008 | <5 | 259.11 | 1 | 23000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-04-20 | 2.23 | 7.4 | 6.5 | T/X | T/X | N/S | 5 | 5 | 968 | 166 | T/X | <0.3 | 17.02 | T/X | N/S | N/S | 276.2 | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.01 | 0.07 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | 88.98 | 31.84 | 353 | 1.2 | N/S
2021-04-21 | 2.39 | 7.4 | 6.4 | T/X | T/X | N/S | 5 | 4 | 1062 | 146 | T/X | 0.3 | 15.89 | T/X | N/S | N/S | 292.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-22 | 2.18 | 7.4 | 6.1 | 10 | 3 | N/S | 4 | 4 | 998 | 140 | T/X | <0.3 | 16.25 | T/X | N/S | N/S | 307.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-23 | 2.15 | 7.4 | 6.3 | N/S | N/S | N/S | <4 | <4 | 1064 | 160 | T/X | <0.3 | 18.21 | T/X | N/S | N/S | 331.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-24 | 2.09 | 7.4 | 5.3 | N/S | N/S | N/S | <4 | <4 | 1172 | 160 | T/X | 0.3 | 19.07 | T/X | N/S | N/S | 371.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-25 | 2.11 | 7.4 | 6.2 | T/X | T/X | N/S | 6 | 5 | 1108 | 116 | T/X | 0.3 | 17.86 | T/X | N/S | N/S | 361 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-26 | 2.15 | 7.4 | 5.6 | 5 | <2 | <5 | <4 | <4 | 1130 | 130 | T/X | <0.3 | 17.39 | T/X | <0.005 | <5 | 369.14 | 1 | 7800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-04-27 | 2.11 | 7.4 | 6.3 | T/X | T/X | N/S | <4 | <4 | 1134 | 150 | T/X | <0.3 | 17.99 | T/X | N/S | N/S | 364.97 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.006 | 0.06 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 97.29 | 33.48 | 381 | 1.3 | N/S
2021-04-28 | 2.17 | 7.3 | 5.9 | T/X | T/X | N/S | 7 | 7 | 1114 | 102 | T/X | <0.3 | 19.63 | T/X | N/S | N/S | 347.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-29 | 2.47 | 7.4 | 6.1 | 10 | 3 | N/S | 5 | 5 | 1142 | 224 | T/X | <0.3 | 16.16 | T/X | N/S | N/S | 334.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-30 | 2.48 | 7.4 | 5.7 | N/S | N/S | N/S | 6 | 5 | 1318 | 216 | T/X | <0.3 | 16.34 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-01 | 2.31 | 7.3 | 7 | N/S | N/S | N/S | 7 | 6 | 1610 | 218 | T/X | <0.3 | 17.29 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-02 | 2.15 | 7.4 | 6.1 | T/X | T/X | N/S | 6 | 6 | 1322 | 220 | T/X | <0.3 | 18.39 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-03 | 2.29 | 7.4 | 5.6 | 23 | 6 | <5 | 20 | 18 | 1516 | 182 | T/X | <0.3 | 16.28 | T/X | 0.005 | 5 | 530.49 | 0.9 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-05-04 | 2.44 | 7.3 | 5.2 | T/X | T/X | N/S | 5 | 4 | 1386 | 140 | T/X | <0.3 | 15.71 | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.008 | 0.07 | 0.05 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 97.11 | 34.24 | 383 | 0.9 | N/S
2021-05-05 | 2.22 | 7.4 | 5 | T/X | T/X | N/S | 7 | 6 | 1252 | 188 | T/X | 0.3 | 15.43 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-06 | 2.11 | 7.5 | 6.8 | 11 | 3 | N/S | 6 | 5 | 1256 | 178 | T/X | 0.4 | 16.56 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-07 | 2.11 | 7.3 | 6.3 | N/S | N/S | N/S | 7 | 5 | 1316 | 170 | T/X | 0.3 | 17 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-08 | 2.12 | 7.3 | 5 | N/S | N/S | N/S | 5 | 5 | 1250 | 172 | T/X | 0.5 | 15.85 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-09 | 4.03 | 7.3 | 5.8 | T/X | T/X | N/S | 5 | 4 | 744 | 106 | T/X | <0.3 | 7.94 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-10 | 4.2 | 7.2 | 5.1 | 7 | 3 | <5 | <4 | <4 | 866 | 112 | T/X | <0.3 | 7.35 | T/X | 0.012 | <5 | 274.58 | 0.5 | 16000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-05-11 | 4.2 | 7.2 | 5.1 | T/X | T/X | N/S | 4 | <4 | 938 | 120 | T/X | 0.6 | 8.17 | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 79.4 | 30.05 | 322 | 2.1 | N/S
2021-05-12 | 3.56 | 7.2 | 5.5 | T/X | T/X | N/S | 5 | <4 | 972 | 128 | T/X | 1.5 | 9.14 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-13 | 2.4 | 7.3 | 5.9 | 16 | 5 | N/S | 12 | 10 | 1080 | 198 | T/X | <0.3 | 13.54 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-14 | 2.43 | 7.2 | 6.2 | N/S | N/S | N/S | 9 | 8 | 1386 | 374 | T/X | <0.3 | 15.72 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-15 | 3.35 | 7.2 | 6.3 | N/S | N/S | N/S | 10 | 8 | 1346 | 344 | T/X | 1.7 | 14.13 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-16 | 2.48 | 7.2 | 6.1 | T/X | T/X | N/S | 9 | 7 | 1422 | 354 | T/X | 0.9 | 13.37 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-17 | 2.4 | 7.3 | 6.6 | 10 | 9 | <5 | 7 | 6 | 1336 | 226 | T/X | <0.3 | 15.92 | T/X | 0.01 | <5 | 404.94 | 0.8 | 2900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-05-18 | 2.4 | 7.3 | 6.7 | T/X | T/X | N/S | 6 | 5 | 1340 | 308 | T/X | <0.3 | 17.58 | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 104.95 | 37.4 | 416 | 0.6 | N/S
2021-05-19 | 2.37 | 7.2 | 6.1 | T/X | T/X | N/S | 4 | <4 | 1352 | 250 | T/X | <0.3 | 17.05 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-20 | 2.38 | 7.3 | 6.3 | T/X | T/X | N/S | <4 | <4 | 1362 | 222 | T/X | <0.3 | 18.23 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-21 | 2.26 | 7.3 | 5.5 | N/S | N/S | N/S | 7 | 6 | 1284 | 248 | T/X | <0.3 | 14.22 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-22 | 2.16 | 7.3 | 5.4 | N/S | N/S | N/S | 5 | 4 | 1236 | 190 | T/X | <0.3 | 12.16 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-23 | 2.19 | 7.3 | 5.8 | T/X | T/X | N/S | 4 | <4 | 1234 | 210 | T/X | 0.6 | 12.36 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-24 | 2.26 | 7.3 | 4.4 | T/X | T/X | <5 | 12 | 10 | 1180 | 176 | T/X | 0.9 | 12 | T/X | 0.006 | <5 | 352.1 | 0.9 | 9800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-05-25 | 2.2 | 7.3 | 5 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | T/X | S/X | S/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S
2021-05-26 | 3.24 | 7.3 | 4.4 | T/X | T/X | N/S | 7 | 6 | 1008 | 124 | T/X | 3.7 | 8.17 | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.006 | 0.09 | N/S | <0.002 | 0.056 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | 85.14 | 30.06 | 336 | N/S | N/S
2021-05-27 | 2.52 | 7.2 | 4.3 | 57 | 12 | N/S | 33 | 29 | 1132 | 176 | T/X | 1.8 | 13.45 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-28 | 3.11 | 7.3 | 6.1 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-29 | 2.98 | 7.1 | 5.6 | N/S | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-30 | 2.69 | 7.2 | 6.9 | T/X | T/X | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-31 | 3.12 | 7.2 | 5.9 | T/X | T/X | <5 | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-01 | 2.81 | 7.2 | 6.5 | T/X | T/X | N/S | 11 | 9 | 958 | 132 | 6 | 1.6 | 13.61 | 3.12 | N/S | <5 | 259.41 | 0.8 | 59000 | <0.002 | 0.039 | <0.002 | <0.004 | 0.022 | 0.28 | 0.05 | <0.002 | 0.039 | 0.002 | <0.004 | <0.004 | 0.049 | <0.002 | <0.002 | <0.002 | <3 | 79.5 | 30.09 | 322 | 1.3 | N/S
2021-06-02 | 2.38 | 7.2 | 5.7 | 14 | 3 | N/S | 4 | 4 | 992 | 128 | <4 | 0.7 | 15.38 | 2.64 | 0.005 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-03 | 2.42 | 7.2 | 5.3 | 6 | <2 | N/S | <4 | <4 | 1228 | 366 | <1 | <0.3 | 16.39 | 0.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-04 | 2.34 | 7.1 | 4.6 | N/S | N/S | N/S | 4 | <4 | 1362 | 374 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-05 | 2.24 | 7.2 | 4.1 | N/S | N/S | N/S | 4 | 4 | 1482 | 414 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-06 | 2.15 | 7.2 | 4.5 | 11 | 4 | N/S | <4 | <4 | 1432 | 374 | <4 | 1.3 | 14.11 | 3.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-07 | 2.16 | 7.3 | 3.8 | 10 | 5 | <5 | 4 | <4 | 1288 | 256 | <4 | 0.7 | 9.61 | 3.49 | <0.005 | <5 | 390.26 | 0.9 | 9700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-06-08 | 2.29 | 7.3 | 3.9 | 12 | 3 | N/S | 4 | <4 | 1204 | 216 | <4 | 0.4 | 5.16 | 2.92 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.007 | 0.06 | N/S | <0.002 | 0.014 | 0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | 106.45 | 36.24 | 415 | 0.8 | N/S
2021-06-09 | 2.15 | 7.3 | 4.6 | 8 | 2 | N/S | <4 | <4 | 1154 | 142 | <4 | 0.3 | 5.2 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-10 | 2.06 | 7.3 | 5 | 20 | 6 | N/S | 22 | 19 | 1196 | 212 | <4 | 0.5 | 7.05 | 3.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-11 | 2.07 | 7.3 | 4.9 | N/S | N/S | N/S | 5 | 5 | 1206 | 198 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-12 | 2.02 | 7.3 | 5.3 | N/S | N/S | N/S | 6 | 5 | 1156 | 192 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-13 | 2.08 | 7.3 | 4.8 | 16 | 4 | N/S | 9 | 7 | 1012 | 186 | 3 | 1.2 | 9.6 | 4.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-14 | 2.11 | 7.3 | 4.5 | 11 | 5 | <5 | 6 | <4 | 1066 | 144 | 2 | 1 | 7.92 | 3.74 | 0.016 | <5 | 307.5 | 0.9 | 59000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-06-15 | 2.02 | 7.3 | 3.8 | 11 | 3 | N/S | 9 | 7 | 1162 | 212 | 2 | 0.7 | 9.25 | 3.75 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.008 | 0.07 | N/S | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 108.94 | 35.79 | 419 | 0.6 | N/S
2021-06-16 | 2.02 | 7.4 | 5 | 9 | 3 | N/S | 4 | <4 | 1222 | 218 | 3 | 1.6 | 11.39 | 3.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-17 | 2.01 | 7.4 | 3.8 | 13 | 5 | N/S | <4 | <4 | 1288 | 258 | 3 | 2.4 | 11.1 | 4.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-18 | 2.07 | 7.3 | 3.6 | N/S | N/S | N/S | <4 | <4 | 1192 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-19 | 2.05 | 7.3 | 3.5 | N/S | N/S | N/S | <4 | <4 | 1096 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-20 | 2.03 | 7.3 | 4.6 | 12 | 3 | N/S | <4 | <4 | 948 | 142 | 4 | 3 | 9.78 | 3.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-21 | 3.58 | 7.2 | 3.5 | 25 | 6 | <5 | 8 | 7 | 834 | 160 | 5 | 3.6 | 5.12 | 2.47 | <0.005 | <5 | 199.65 | 0.7 | 8500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-06-22 | 2.17 | 7.2 | 4.5 | 12 | 3 | N/S | 4 | <4 | 916 | 180 | 3 | 2 | 9.58 | 2.32 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.006 | 0.09 | N/S | <0.002 | 0.034 | <0.002 | 0.005 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | 73.27 | 27.57 | 296 | 0.7 | N/S
2021-06-23 | 2.12 | 7.3 | 4.9 | 19 | 4 | N/S | 6 | 5 | 1008 | 240 | 3 | 1.2 | 12.29 | 2.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-24 | 2.07 | 7.3 | 4.4 | 15 | 4 | N/S | 8 | 7 | 1054 | 294 | 3 | 1.2 | 13.94 | 3.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-25 | 3.6 | 7.2 | 5.2 | N/S | N/S | N/S | 8 | 7 | 736 | 210 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-26 | 4.2 | 7.1 | 4.3 | N/S | N/S | N/S | 7 | 6 | 704 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-27 | 4.2 | 7.2 | 4.6 | 6 | 2 | N/S | <4 | <4 | 738 | 216 | 1 | 0.3 | 8.42 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-28 | 4.09 | 7.2 | 4.6 | 9 | 3 | <5 | 6 | 5 | 768 | 184 | 2 | 1.7 | 9.17 | 1.5 | <0.005 | <5 | 156.09 | 0.5 | 220000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-06-29 | 4.12 | 7.4 | 4.8 | 5 | <2 | N/S | 4 | <4 | 672 | 184 | <1 | 0.4 | 9.29 | 1.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.03 | <0.002 | <0.004 | 0.005 | 0.08 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | 65.65 | 25.15 | 267 | 0.9 | N/S
2021-06-30 | 4.2 | 7.1 | 4.5 | 4 | <2 | N/S | <4 | <4 | 690 | 168 | <1 | <0.3 | 9.58 | 1.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-01 | 4.19 | 7.2 | 4.8 | 4 | <2 | N/S | <4 | <4 | 714 | 158 | 1 | <0.3 | 11.68 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-02 | 3.64 | 7.2 | 4.1 | N/S | N/S | N/S | <4 | <4 | 994 | 272 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-03 | 3.27 | 7.3 | 4.3 | N/S | N/S | N/S | <4 | <4 | 1040 | 274 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-04 | 3.71 | 7.3 | 4.5 | T/X | T/X | N/S | <4 | <4 | 898 | 126 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-05 | 2.53 | 7.2 | 4.4 | 5 | <2 | <5 | <4 | <4 | 876 | 150 | 2 | 0.8 | 12.89 | 2.08 | <0.005 | <5 | 230.57 | 0.7 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-06 | 2.65 | 7.3 | 3 | 7 | <2 | N/S | <4 | <4 | 920 | 148 | 3 | 2.1 | 10.92 | 2.36 | N/S | N/S | N/S | N/S | 91000 | <0.002 | 0.041 | <0.002 | <0.004 | 0.007 | 0.07 | 0.05 | <0.002 | 0.039 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | T/X | 87.55 | 31.7 | 349 | 0.9 | N/S
2021-07-07 | 2.28 | 7.2 | 3.7 | 6 | <2 | N/S | <4 | <4 | 942 | 152 | T/X | 0.5 | 13.85 | 2.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-08 | 2.18 | 7.2 | 4 | 9 | 3 | N/S | 8 | 7 | 984 | 116 | 2 | 0.6 | 12.89 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-07-09 | 2.28 | 7.3 | 5.4 | N/S | N/S | N/S | 7 | 5 | 978 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-10 | 2.34 | 7.3 | 5.1 | N/S | N/S | N/S | 6 | 5 | 978 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-11 | 2.34 | 7.3 | 4.6 | 8 | 3 | N/S | 6 | 4 | 1062 | 186 | 2 | 0.4 | 13.05 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-12 | 2.34 | 7.2 | 4 | 8 | <2 | <5 | 6 | 5 | 1106 | 222 | 2 | 0.4 | 13.49 | 2.65 | <0.005 | <5 | 284.47 | 0.8 | 7900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-07-13 | 2.33 | 7.2 | 4.3 | 6 | <2 | N/S | 6 | 4 | 1092 | 228 | 1 | <0.3 | 15.64 | 2.98 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.006 | 0.09 | N/S | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 93.24 | 33.09 | 369 | 0.5 | N/S
2021-07-14 | 2.25 | 7.1 | 4.1 | 5 | <2 | N/S | <4 | <4 | 1074 | 208 | 1 | <0.3 | 16.02 | 2.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-15 | 2.25 | 7.3 | 3.6 | 5 | 3 | N/S | <4 | <4 | 1146 | 180 | <1 | <0.3 | 14.9 | 3.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-16 | 2.26 | 7.2 | 3.7 | N/S | N/S | N/S | <4 | <4 | 1210 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-17 | 2.05 | 7.3 | 4.7 | N/S | N/S | N/S | <4 | <4 | 1220 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-18 | 2.08 | 7.3 | 4.6 | 4 | <2 | N/S | <4 | <4 | 1208 | 210 | 2 | <0.3 | 14.47 | 3.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-19 | 2.01 | 7.2 | 3.4 | 5 | <2 | <5 | <4 | <4 | 1106 | 138 | <1 | <0.3 | 14.72 | 3.23 | <0.005 | <5 | 352.91 | 0.9 | 18000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-07-20 | 2.02 | 7.3 | 4 | 5 | <2 | N/S | <4 | <4 | 1082 | 146 | 1 | <0.3 | 14.7 | 3.08 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.004 | 0.06 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | 86.88 | 30.61 | 343 | 0.9 | N/S
2021-07-21 | 1.97 | 7.2 | 3.8 | 4 | <2 | N/S | <4 | <4 | 1046 | 178 | 1 | <0.3 | 16.38 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-22 | 1.92 | 7.3 | 4.8 | 5 | 3 | N/S | 6 | 5 | 1018 | 170 | 2 | <0.3 | 17.69 | 3.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-23 | 1.99 | 7.2 | 4.4 | N/S | N/S | N/S | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-24 | 2.05 | 7.3 | 4.4 | N/S | N/S | N/S | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-25 | 2.04 | 7.2 | 4.3 | 7 | 3 | N/S | 4 | <4 | 970 | 166 | <1 | <0.3 | 19.33 | 3.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-26 | 2.02 | 7.2 | 4.4 | 6 | <2 | <5 | 5 | 4 | 958 | 134 | T/X | <0.3 | 20.58 | T/X | <0.005 | <5 | 237.61 | 0.9 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-07-27 | 2.02 | 7.2 | 4.7 | 7 | 3 | N/S | 6 | 4 | 1104 | 180 | T/X | <0.3 | 20.09 | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.006 | 0.07 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.041 | <0.002 | <0.002 | <0.002 | N/S | 88.35 | 30.63 | 347 | <0.5 | N/S
2021-07-28 | 2.16 | 7.2 | 4.7 | 8 | 5 | N/S | 5 | 4 | 1004 | 154 | 1 | <0.3 | 18.29 | 3.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-29 | 2.39 | 7.2 | 4.3 | 5 | 2 | N/S | 4 | <4 | 926 | 154 | <1 | <0.3 | 16.4 | 3.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-30 | 2.41 | 7.3 | 4 | N/S | N/S | N/S | <4 | <4 | 1152 | 234 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-31 | 2.21 | 7.2 | 3.7 | N/S | N/S | N/S | 4 | <4 | 1232 | 264 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-01 | 2.03 | 7.3 | 3.7 | 3 | <2 | N/S | <4 | <4 | 1208 | 196 | <1 | <0.3 | 24.29 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-02 | 1.87 | 7.3 | 4.7 | 3 | <2 | <5 | <4 | <4 | 1160 | 236 | <1 | <0.3 | 25.07 | 3.1 | <0.005 | <5 | 305.86 | 0.9 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-08-03 | 1.88 | 7.3 | 4.2 | <2 | <2 | N/S | <4 | <4 | 1142 | 268 | <2 | <0.3 | 24.24 | 3.76 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.05 | 0.04 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | 94.53 | 31.53 | 366 | <0.5 | N/S
2021-08-04 | 1.96 | 7.3 | 3.4 | 3 | <2 | N/S | <4 | <4 | 1114 | 212 | <2 | 0.4 | 22.96 | 3.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-05 | 2.06 | 7.2 | 4.8 | 5 | 3 | N/S | 4 | 4 | 1204 | 282 | <2 | <0.3 | 21.33 | 3.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-06 | 1.93 | 7.2 | 4.4 | N/S | N/S | N/S | 4 | <4 | 1190 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-07 | 2.04 | 7.2 | 4.6 | N/S | N/S | N/S | 5 | 4 | 1250 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-08 | 2.01 | 7.2 | 3.4 | T/X | T/X | N/S | 5 | 4 | 1208 | 202 | <4 | <0.3 | 22.8 | 3.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-09 | 2.13 | 7.1 | 4 | 4 | <2 | <5 | 6 | 4 | 1190 | 208 | <1 | <0.3 | 20.48 | 3.78 | 0.005 | 7 | 340.36 | 0.9 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-08-10 | 2 | 7.2 | 4.2 | 3 | 2 | N/S | 6 | <4 | 1166 | 190 | <1 | 0.3 | 20.48 | 3.56 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 100.41 | 31.32 | 380 | 0.8 | N/S
2021-08-11 | 2.25 | 7.2 | 3.8 | 4 | 2 | N/S | 6 | <4 | 1130 | 210 | <1 | <0.3 | 20.69 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-12 | 2.25 | 7.2 | 2 | 6 | 4 | N/S | 7 | 6 | 1102 | 172 | 1 | <0.3 | 21.04 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-13 | 2.1 | 7.2 | 3.8 | N/S | N/S | N/S | <4 | 4 | 1132 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-14 | 1.99 | 7.2 | 3.9 | N/S | N/S | N/S | 4 | 4 | 1156 | 236 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-15 | 1.92 | 7.2 | 4.1 | 5 | 2 | N/S | 6 | 4 | 1064 | 150 | 1 | 0.4 | 24.24 | 3.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-16 | 1.93 | 7.2 | 4 | 5 | 3 | <5 | 6 | 5 | 1058 | 234 | <2 | <0.3 | 24.14 | 3.73 | 0.01 | 5 | 261.08 | 1 | 66000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-08-17 | 1.89 | 7.2 | 3.8 | 3 | 4 | N/S | 6 | 6 | 1062 | 220 | 2 | <0.3 | 24.05 | 3.69 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.008 | 0.08 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.042 | <0.002 | <0.002 | <0.002 | N/S | 83.99 | 28.44 | 327 | 0.5 | N/S
2021-08-18 | 1.94 | 7.2 | 3.8 | 3 | 3 | N/S | 6 | 5 | 1118 | 242 | 2 | <0.3 | 23.41 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-19 | 1.93 | 7.3 | 4 | 5 | 3 | N/S | 5 | 4 | 1128 | 282 | T/X | <0.3 | 22 | 3.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-20 | 2.09 | 7.1 | 4 | N/S | N/S | N/S | 5 | 4 | 1042 | 228 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-21 | 2.38 | 7.1 | 3.7 | N/S | N/S | N/S | <4 | 4 | 986 | 228 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-22 | 2.68 | 7.1 | 4 | 4 | 2 | N/S | 5 | 4 | 838 | 142 | <1 | <0.3 | 15.57 | 1.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-23 | 2.16 | 7.1 | 3.8 | <2 | <2 | <5 | 4 | <4 | 1000 | 200 | <4 | <0.3 | 19.59 | 2.96 | <0.005 | 7 | 245.82 | 0.8 | 5900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-08-24 | 2.16 | 7.1 | 3.8 | 2 | 2 | N/S | 4 | <4 | 1010 | 200 | <4 | <0.3 | 21.33 | 3.52 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.007 | 0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | 77.88 | 27.08 | 306 | <0.5 | N/S
2021-08-25 | 2.48 | 7.2 | 3.8 | 4 | 3 | N/S | 4 | 4 | 916 | 220 | <1 | <0.3 | 19.52 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-26 | 3.89 | 7.1 | 4.1 | 3 | 3 | N/S | 5 | 4 | 756 | 162 | <1 | <0.3 | 14.14 | 1.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-27 | 3.83 | 7 | 3.7 | N/S | N/S | N/S | 4 | 4 | 926 | 218 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-28 | 2.54 | 7.1 | 3.3 | N/S | N/S | N/S | <4 | <4 | 1088 | 260 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-29 | 2.21 | 7.2 | 4.1 | T/X | T/X | N/S | 4 | 4 | 1124 | 258 | T/X | <0.3 | 17.83 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-30 | 2.21 | 7.1 | 4 | T/X | T/X | <5 | 4 | <4 | 1200 | 264 | <1 | <0.3 | 19.21 | 2.71 | <0.005 | 12 | 334.89 | 0.8 | 16000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-08-31 | 2.2 | 7.1 | 3.9 | T/X | T/X | N/S | 4 | 4 | 1276 | 292 | T/X | <0.3 | 19.55 | 2.56 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 103.79 | 34.44 | 401 | 0.6 | N/S
2021-09-01 | 2.13 | 7 | 3.9 | T/X | T/X | N/S | 4 | <4 | 1426 | 260 | <1 | <0.3 | 20.19 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-02 | 2.01 | 7.1 | 3.9 | T/X | T/X | N/S | <4 | <4 | 1404 | 284 | <1 | <0.3 | 19.2 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-03 | 1.94 | 7.2 | 4.1 | N/S | N/S | N/S | <4 | <4 | 1372 | 310 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-04 | 1.87 | 7.2 | 3.6 | N/S | N/S | N/S | <4 | <4 | 1438 | 366 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-05 | 1.87 | 7.2 | 4 | T/X | T/X | N/S | <4 | <4 | 1408 | 346 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-06 | 1.82 | 7.2 | 4.1 | 7 | <2 | <5 | <4 | <4 | 1338 | 282 | <1 | <0.3 | 20.69 | <0.15 | 0.005 | <5 | 342.62 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-07 | 2.15 | 7.1 | 4 | 8 | 3 | N/S | <4 | <4 | 1176 | 212 | <1 | 0.3 | 19.53 | 3.25 | N/S | N/S | N/S | N/S | 3300 | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.07 | 0.04 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | <3 | 92.36 | 32.03 | 363 | <0.5 | N/S
2021-09-08 | 2.31 | 7.1 | 3.7 | 5 | <2 | N/S | <4 | <4 | 1030 | 198 | <1 | <0.3 | 18.22 | 2.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-09 | 2.1 | 7.2 | 4.4 | 5 | <2 | N/S | <4 | <4 | 1046 | 160 | 1 | <0.3 | 19.59 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-10 | 1.92 | 7.3 | 3.7 | N/S | N/S | N/S | <4 | <4 | 1046 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-11 | 1.84 | 7.2 | 3.6 | N/S | N/S | N/S | 4 | <4 | 1074 | 204 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-12 | 1.96 | 7.2 | 3.5 | N/S | N/S | N/S | <4 | <4 | 1094 | 166 | 1 | <0.3 | 21.4 | 3.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-13 | 1.79 | 7.2 | 3.5 | T/X | T/X | <5 | <4 | 5 | 1224 | 298 | 1 | <0.3 | 19.22 | 3.28 | 0.008 | <5 | 277.07 | 0.9 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-09-14 | 1.66 | 7.3 | 3.6 | T/X | T/X | N/S | <4 | 4 | 1132 | 230 | 1 | <0.3 | 20.8 | 3.6 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.038 | <0.002 | <0.002 | <0.002 | N/S | 86.37 | 29.32 | 336 | <0.5 | N/S
2021-09-15 | 2.08 | 7.1 | 3.8 | T/X | T/X | N/S | <4 | 4 | 1218 | 314 | 1 | <0.3 | 24.76 | 3.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-16 | 2.11 | 7.1 | 3.9 | T/X | T/X | N/S | 4 | 4 | 1344 | 344 | 1 | <0.3 | 23.77 | 3.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-17 | 1.92 | 7.3 | 4.3 | N/S | N/S | N/S | 6 | 5 | 1418 | 382 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-18 | 1.84 | 7.2 | 3.6 | N/S | N/S | N/S | 9 | 8 | 1452 | 414 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-19 | 1.88 | 7.3 | 3.5 | N/S | N/S | N/S | 8 | 6 | 1450 | 428 | 1 | <0.3 | 24.3 | 3.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-20 | 1.91 | 7.3 | 3.2 | 11 | 4 | <5 | 6 | 6 | 1328 | 296 | <1 | <0.3 | 22.14 | 3.4 | <0.005 | <5 | 362.01 | 0.9 | 8300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-09-21 | 2.06 | 7.2 | 4.5 | 9 | 4 | N/S | 5 | 4 | 1322 | 322 | <1 | <0.3 | 18.03 | 2.97 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | 120.32 | 38.38 | 458 | 2.3 | N/S
2021-09-22 | 2.16 | 7.2 | 3.9 | 10 | 5 | N/S | 8 | 8 | 1210 | 228 | 1 | <0.3 | 18.42 | 4.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-23 | 1.97 | 7.1 | 4 | 13 | 5 | N/S | 8 | 6 | 1282 | 246 | 1 | <0.3 | 19.46 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-24 | 2.17 | 7.3 | 4.1 | N/S | N/S | N/S | <4 | <4 | 1404 | 286 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-25 | 2.01 | 7.2 | 3.7 | N/S | N/S | N/S | 8 | 7 | 1312 | 250 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-26 | 1.82 | 7.2 | 4.1 | N/S | N/S | N/S | 5 | 4 | 1272 | 238 | 1 | <0.3 | 20.94 | 3.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-27 | 1.84 | 7.2 | 3.8 | 8 | 3 | <5 | 5 | 4 | 1326 | 222 | <1 | <0.3 | 19.59 | 3.1 | <0.005 | <5 | 361.03 | 0.9 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-09-28 | 1.87 | 7.6 | 3.8 | 7 | 3 | N/S | <4 | <4 | 1298 | 254 | <1 | <0.3 | 19.47 | 3.29 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | 104.57 | 34.77 | 404 | 0.5 | N/S
2021-09-29 | 1.92 | 7.1 | 3.8 | 8 | 5 | N/S | 4 | <4 | 1220 | 160 | <1 | <0.3 | 20.21 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-30 | 1.83 | 7.4 | 4 | 8 | 5 | N/S | <4 | <4 | 1262 | 226 | 1 | <0.3 | 19.59 | 3.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-01 | 1.93 | 7.4 | 4.5 | N/S | N/S | N/S | <4 | <4 | 1394 | 284 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-02 | 1.85 | 7.4 | 3.8 | N/S | N/S | N/S | 5 | 5 | 1430 | 306 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-03 | 1.86 | 7.3 | 3.9 | N/S | N/S | N/S | 4 | <4 | 1346 | 318 | 1 | <0.3 | 19.58 | 3.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-04 | 2 | 7.2 | 3.8 | 7 | 3 | <5 | 6 | 5 | 1382 | 276 | 2 | <0.3 | 22.08 | 3.83 | <0.005 | <5 | 398.69 | 1 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-10-05 | 1.87 | 7.5 | 4 | 6 | 3 | N/S | 6 | 5 | 1388 | 266 | 1 | <0.3 | 22.44 | 4.05 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.007 | 0.07 | 0.04 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.046 | <0.002 | <0.002 | <0.002 | N/S | 111.13 | 36.36 | 427 | <0.5 | N/S
2021-10-06 | 1.9 | 7.4 | 3.9 | 6 | 3 | N/S | 6 | 4 | 1326 | 202 | <1 | <0.3 | 23.89 | 3.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-07 | 1.92 | 7.4 | 3.8 | 8 | 3 | N/S | 8 | 6 | 1318 | 256 | 1 | <0.3 | 23.64 | 3.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-08 | 2.15 | 7.3 | 4 | N/S | N/S | N/S | 6 | 5 | 1272 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-09 | 2.15 | 7.3 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1318 | 314 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-10 | 2.08 | 7.4 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1284 | 296 | <1 | <0.3 | 25.53 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-11 | 2.01 | 7.3 | 7.3 | 5 | 2 | <5 | <4 | <4 | 1168 | 238 | <1 | 0.3 | 26.05 | 3.46 | <0.005 | <5 | 328.55 | 0.9 | 600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-10-12 | 3.2 | 7.4 | 7.6 | 5 | <2 | N/S | <4 | <4 | 952 | 212 | <1 | <0.3 | 18.65 | 2.9 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.029 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 80.37 | 27.69 | 315 | 0.7 | N/S
2021-10-13 | 2.96 | 7.3 | 7.4 | 4 | <2 | N/S | <4 | <4 | 936 | 198 | 1 | <0.3 | 16.53 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-14 | 3.37 | 7.3 | 7.3 | 6 | 3 | N/S | 5 | 4 | 890 | 154 | 1 | <0.3 | 14.01 | 2.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-15 | 1.98 | 7.4 | 7.7 | N/S | N/S | N/S | 4 | <4 | 900 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-16 | 1.95 | 7.4 | 3.6 | N/S | N/S | N/S | 6 | 4 | 976 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-17 | 2.03 | 7.5 | 3.7 | N/S | N/S | N/S | 7 | 5 | 998 | 178 | 1 | <0.3 | 24.23 | 3.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-18 | 2.14 | 7.2 | 8 | 7 | 3 | <5 | 5 | 5 | 1028 | 144 | 1 | <0.3 | 23.09 | 3.43 | <0.005 | <5 | 242.13 | 0.9 | 41000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-10-19 | 1.88 | 7.4 | 7.9 | 8 | 4 | N/S | 6 | 5 | 1014 | 124 | 2 | <0.3 | 23.16 | 3.62 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.007 | 0.08 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 81.66 | 29.39 | 325 | 1.1 | N/S
2021-10-20 | 1.75 | 7.5 | 7.5 | 8 | 6 | N/S | 7 | 6 | 1082 | 154 | 1 | <0.3 | 24.79 | 3.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-21 | 1.8 | 7.4 | 7.6 | 10 | 9 | N/S | 6 | 5 | 1174 | 212 | 2 | <0.3 | 22.44 | 3.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-22 | 1.8 | 7.4 | 7.6 | N/S | N/S | N/S | 7 | 5 | 1206 | 210 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-23 | 1.77 | 7.5 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1266 | 248 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-24 | 2.48 | 7.4 | 7.6 | N/S | N/S | N/S | 7 | 5 | 1062 | 182 | 1 | <0.3 | 19.12 | 3.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-25 | 4.2 | 7.1 | 7.3 | 14 | 5 | <5 | 14 | 11 | 628 | 100 | 2 | <0.3 | 8.43 | 1.36 | <0.005 | <5 | 161.62 | 0.4 | 140000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-10-26 | 4.2 | 7.2 | 7.5 | 7 | 3 | N/S | 5 | <4 | 752 | 156 | <1 | <0.3 | 9.07 | 1.02 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.028 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.005 | 0.005 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | 65.05 | 23.53 | 259 | 1.4 | N/S
2021-10-27 | 4.02 | 7.2 | 7.4 | 6 | 2 | N/S | 6 | 4 | 806 | 146 | <1 | <0.3 | 11.56 | 1.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-28 | 3.94 | 7.3 | 7.5 | 7 | 3 | N/S | 8 | 6 | 874 | 138 | <1 | <0.3 | 12.96 | 1.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-29 | 4.05 | 7.2 | 7.1 | N/S | N/S | N/S | 12 | 9 | 820 | 104 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-30 | 4.2 | 7.2 | 7.1 | N/S | N/S | N/S | 4 | <4 | 734 | 102 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-31 | 4.04 | 7.2 | 7.2 | N/S | N/S | N/S | 11 | 9 | 798 | 112 | 1 | <0.3 | 13.16 | 1.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-01 | 3.49 | 7.2 | 7.5 | 4 | 3 | <5 | 9 | 8 | 898 | 118 | 2 | <0.3 | 14.29 | 2.03 | <0.005 | <5 | 258.09 | 0.6 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-11-02 | 2.29 | 7.3 | 7.7 | 4 | 4 | N/S | 8 | 7 | 1016 | 134 | 1 | <0.3 | 16.4 | 2.41 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.01 | 0.11 | 0.04 | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 88.75 | 31.58 | 352 | 0.9 | N/S
2021-11-03 | 2.04 | 7.4 | 7.9 | T/X | T/X | N/S | 4 | 4 | 1056 | 162 | <1 | <0.3 | 20.72 | 0.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-04 | 2.06 | 7.4 | 7.9 | T/X | T/X | N/S | 6 | 5 | 1120 | 196 | 1 | <0.3 | 22.01 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-05 | 2.05 | 7.3 | 7.8 | N/S | N/S | N/S | 4 | <4 | 1138 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-06 | 2.54 | 7.3 | 7.7 | N/S | N/S | N/S | 5 | 5 | 1202 | 178 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-07 | 2.12 | 7.4 | 7.1 | N/S | N/S | N/S | 5 | 4 | 1172 | 152 | 1 | 0.5 | 18.09 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-08 | 1.9 | 7.4 | 7.6 | 5 | <2 | <5 | 4 | <4 | 1166 | 180 | 1 | <0.3 | 20.4 | 3.14 | <0.005 | <5 | 345.97 | 0.9 | 8200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-11-09 | 1.37 | 7.4 | 7.5 | 6 | 3 | N/S | 5 | 4 | 1162 | 156 | 1 | <0.3 | 22.06 | 3.18 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.008 | 0.08 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 91.75 | 30.79 | 356 | <0.5 | N/S
2021-11-10 | 1.86 | 7.4 | 7.5 | 16 | 7 | N/S | 16 | 13 | 1144 | 194 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-11 | 2.34 | 7.5 | 7.3 | 15 | 6 | N/S | 14 | 11 | 972 | 188 | 2 | <0.3 | 18.91 | 3.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-12 | 3.03 | 7.2 | 7.7 | N/S | N/S | N/S | 23 | 19 | 960 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-13 | 2.81 | 7.2 | 6.9 | N/S | N/S | N/S | 25 | 21 | 1078 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-14 | 2.21 | 7.5 | 7.6 | N/S | N/S | N/S | 23 | 19 | 1100 | 162 | 2 | <0.3 | 18.45 | 2.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-15 | 2.05 | 7.4 | 7.5 | 12 | 7 | <5 | 20 | 17 | 1086 | 196 | 2 | <0.3 | 19.1 | 2.69 | <0.005 | <5 | 340.81 | 0.8 | 2400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-11-16 | 1.98 | 7.3 | 7.5 | 14 | 8 | N/S | 18 | 15 | 1132 | 184 | 2 | <0.3 | 21.87 | 3.1 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.013 | 0.19 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 91.41 | 32.23 | 361 | <0.5 | N/S
2021-11-17 | 2.16 | 7.3 | 7.6 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-18 | 2.12 | 7.4 | 8 | 12 | 6 | N/S | 8 | 7 | 1030 | 172 | 2 | <0.3 | 19.52 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-19 | 1.99 | 7.4 | 8 | N/S | N/S | N/S | 6 | 5 | 988 | 134 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-20 | 2.01 | 7.4 | 8 | N/S | N/S | N/S | 4 | 4 | 958 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-21 | 2.04 | 7.5 | 7.9 | N/S | N/S | N/S | 4 | <4 | 936 | 116 | 1 | <0.3 | 22.76 | 3.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-22 | 1.99 | 7.5 | 7.5 | T/X | T/X | <5 | 5 | 4 | 978 | 138 | 1 | <0.3 | 22.93 | 3.1 | <0.005 | <5 | 244.6 | 0.9 | 4700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-11-23 | 2.03 | 7.4 | 8 | T/X | T/X | N/S | 5 | 4 | 1034 | 116 | 1 | <0.3 | 23.4 | 3.19 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.007 | 0.08 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.037 | <0.002 | <0.002 | <0.002 | N/S | 90.38 | 30.36 | 351 | <0.5 | N/S
2021-11-24 | 2.03 | 7.3 | 8.1 | 11 | 6 | N/S | 13 | 11 | 1148 | 196 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-25 | 2.16 | 7.3 | 7.9 | 11 | 6 | N/S | 9 | 9 | 1126 | 180 | 2 | 0.3 | 20.19 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-26 | 1.94 | 7.3 | 7.8 | N/S | N/S | N/S | 9 | 7 | 1162 | 178 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-27 | 1.98 | 7.3 | 8 | N/S | N/S | N/S | 10 | 8 | 1146 | 178 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-28 | 2.03 | 7.2 | 7.5 | N/S | N/S | N/S | 10 | 7 | 1128 | 148 | 2 | 0.4 | 22.49 | 3.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-29 | 1.9 | 7.8 | 8.8 | 11 | 5 | <5 | 12 | 10 | 1142 | 194 | 2 | <0.3 | 22.16 | 3.39 | 0.007 | <5 | 332.91 | 0.9 | 3200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-11-30 | 1.87 | 7.2 | 7.8 | 8 | 4 | N/S | 4 | 4 | 1198 | 194 | <1 | <0.3 | 22.94 | 3.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.007 | 0.08 | N/S | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 99.94 | 32.92 | 385 | 0.7 | N/S
2021-12-01 | 1.86 | 7.2 | 8 | T/X | T/X | N/S | 5 | 4 | 1224 | 198 | 1 | <0.3 | 24.23 | 3.46 | N/S | N/S | 372.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-02 | 1.87 | 7.2 | 7.6 | T/X | T/X | N/S | 13 | 11 | 1216 | 180 | 2 | <0.3 | 23.66 | 3.57 | N/S | N/S | 381.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-03 | 1.83 | 7.2 | 7.9 | N/S | N/S | N/S | 8 | 7 | 1188 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | 389.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-04 | 1.89 | 7.4 | 7.3 | N/S | N/S | N/S | 9 | 7 | 1166 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | 364.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-05 | 2.21 | 7.2 | 7.6 | N/S | N/S | N/S | 12 | 10 | 1100 | 190 | 3 | T/X | T/X | 3.48 | N/S | N/S | 375.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-06 | 2.01 | 7.1 | 7.3 | 10 | 6 | <5 | 8 | 8 | 1136 | 152 | 2 | 0.3 | 19.14 | 3 | <0.005 | 7 | 347.14 | 0.9 | 24000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-12-07 | 1.88 | 7.1 | 7.9 | 14 | 8 | N/S | 21 | 17 | 1146 | 168 | 3 | <0.3 | 21.52 | 2.97 | N/S | N/S | 346.47 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.011 | 0.14 | 0.05 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | 86.05 | 28.43 | 332 | 0.7 | N/S
2021-12-08 | 1.85 | 7.1 | 7.8 | 8 | 5 | N/S | 8 | 7 | 1112 | 148 | <1 | <0.3 | 23.44 | 2.93 | N/S | N/S | 330.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-09 | 1.84 | 7.2 | 7.8 | 11 | 8 | N/S | 17 | 15 | 1158 | 138 | 1 | <0.3 | 23.62 | 3.35 | N/S | N/S | 344.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-10 | 2.25 | 7.2 | 7.6 | N/S | N/S | N/S | 19 | 17 | 1140 | 206 | N/S | N/S | N/S | N/S | N/S | N/S | 343.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-11 | 3.96 | 7 | 7.6 | N/S | N/S | N/S | 26 | 23 | 846 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | 238.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-12 | 4.25 | 7 | 6.6 | N/S | N/S | N/S | 17 | 16 | 872 | 174 | 2 | 0.4 | 11.21 | 1.46 | N/S | N/S | 240.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-13 | 3.37 | 7.1 | 6.7 | 21 | 13 | <5 | 19 | 16 | 1004 | 168 | 4 | T/X | T/X | 1.93 | <0.005 | <5 | 292.09 | 0.7 | 30000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-12-14 | 2.3 | 7.3 | 7.8 | 9 | 5 | N/S | 13 | 11 | 1008 | 104 | <1 | <0.3 | 14.56 | 2.11 | N/S | N/S | 297.14 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.008 | 0.11 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 82.57 | 29.32 | 327 | 1.1 | N/S
2021-12-15 | 2.23 | 7.3 | 7.7 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | N/S
2021-12-16 | 2.35 | 7.3 | 7.8 | T/X | T/X | N/S | 13 | 11 | 1056 | 138 | 2 | <0.3 | 16.63 | 2.56 | N/S | N/S | 311.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-17 | 2.13 | 7.2 | 8.2 | N/S | N/S | N/S | 5 | 4 | 1066 | 114 | N/S | N/S | N/S | N/S | N/S | N/S | 315.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-18 | 2.34 | 7.4 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1106 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 332.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-19 | 2.26 | 7.3 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1102 | 90 | <1 | 0.5 | 18.22 | 2.86 | N/S | N/S | 338.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-20 | 2.16 | 7.2 | 8 | 3 | <2 | <5 | <4 | <4 | 1188 | N/S | 1 | <0.3 | 18.45 | 3.24 | <0.005 | <5 | 349.7 | 0.9 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-12-21 | 2.19 | 7.3 | 8.1 | 22 | 21 | N/S | 6 | 5 | 1224 | 198 | <1 | <0.3 | 19.42 | 3.17 | N/S | N/S | 363.07 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.006 | 0.07 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 94.7 | 32.36 | 370 | 0.8 | N/S
2021-12-22 | 2.12 | 7.3 | 8.2 | T/X | T/X | N/S | 4 | 4 | 1174 | 158 | <1 | 0.6 | 18.29 | 3.35 | N/S | N/S | 348.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-23 | 2.18 | 7.2 | 7.9 | T/X | T/X | N/S | 6 | 5 | 1102 | 152 | T/X | T/X | T/X | T/X | N/S | N/S | 318.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-24 | 2.26 | 7.4 | 7.1 | N/S | N/S | N/S | 7 | 6 | 1096 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 329.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-25 | 2.14 | 7.3 | 7 | N/S | N/S | N/S | 6 | 6 | 1102 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | 323.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-26 | 2.19 | 7.6 | 7.3 | N/S | N/S | N/S | 10 | 9 | 1064 | 122 | 3 | 2.2 | 14.16 | 3.78 | N/S | N/S | 322.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-27 | 3.07 | 7.2 | 7.3 | T/X | T/X | <5 | 22 | 18 | 948 | 144 | 3 | 0.6 | 10.4 | 3.36 | <0.005 | <5 | 271.22 | 0.8 | 3800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2021-12-28 | 2.85 | 7.2 | 7.8 | T/X | T/X | N/S | 8 | 6 | 1076 | 140 | 1 | 0.3 | 10.46 | 2.43 | N/S | N/S | 338.67 | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.02 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | 85.49 | 30.76 | 340 | 0.7 | N/S
2021-12-29 | 3.09 | 7.2 | 7.7 | 6 | 3 | N/S | <4 | <4 | 1188 | 94 | 1 | <0.3 | 9.51 | 2.12 | N/S | N/S | 435 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-30 | 3.17 | 7.2 | 7.8 | T/X | T/X | N/S | 5 | 4 | 1168 | 118 | T/X | T/X | T/X | T/X | N/S | N/S | 406.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-31 | 1.87 | 7.2 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1078 | 126 | N/S | N/S | N/S | N/S | N/S | N/S | 360.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
RL effective 1/1/21 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 |  | 1 | 0.3 | 0.25 | 0.15 | 0.005 | 5 | 0.5 | 0.1 | 10 | 0.001 | 0.002 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5
Observations | 365 | 351 | 365 | 142 | 144 | 51 | 335 | 335 | 329 | 328 | 139 | 260 | 260 | 143 | 52 | 51 | 178 | 52 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 50 | 0
Minimum | 1.33 | 7 | 2 | <2 | <2 | <5 | <4 | <4 | 628 | 86 | <1 | <0.3 | 5.12 | <0.15 | <0.005 | <5 | 156.09 | 0.4 | 600 | <0.002 | 0.028 | <0.002 | <0.004 | 0.004 | 0.05 | 0.04 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | <3 | 65.05 | 23.53 | 259 | <0.5
Mean | 2.41 | 7.3 | 5.7 | <9 | <4 | <4 | <7 | <6 | 1154 | 191 | <2 | <0.5 | 17.27 | <2.96 | <0.005 | <4 | 391.68 | 0.8 | GM=10859 | <0.001 | 0.039 | <0.001 | <0.003 | 0.009 | 0.09 | 0.05 | <0.001 | 0.014 | <0.002 | <0.003 | <0.003 | 0.033 | <0.001 | <0.001 | <0.001 | <2 | 90.78 | 31.98 | 358 | <0.9
Maximum | 4.25 | 7.8 | 8.8 | 57 | 21 | <5 | 38 | 35 | 2584 | 428 | 6 | 3.7 | 26.05 | 4.3 | 0.016 | 12 | 1263.34 | 1 | 220000 | <0.002 | 0.059 | <0.002 | <0.004 | 0.026 | 0.28 | 0.06 | <0.002 | 0.056 | 0.005 | 0.005 | <0.004 | 0.066 | <0.002 | <0.002 | <0.002 | <3 | 120.32 | 38.38 | 458 | 2.5
%>400=100
*Effective 1/1/21, means are no longer calculated using the Reporting Limit value in place of non-detect/<LOQ results and are now calculated by replacing any non-detect/<LOQ results with the Reporting Limit/(SQRT2).
January 1-24, 2021, TS, VTS, NH3, NO2+NO3, T/X: Minimal staffing due to COVID-19.
January 4, 2021, PHENOL, T/X: Sample was not sent to lab for analysis.
January 11, 2021, PHENOL, T/X: Analysis performed on the wrong aliquot.
January 14, 2021, BOD5, CBOD, T/X: LCS failure.
January 18, 2021, Cl: Sample MS/MSD recovery failed but LCS passed.
January 25, 2021, BOD5, CBOD, T/X: Dilution water blank failure.
January 2021, ALL OTHER BOD5, CBOD, SS, VSS, T/X: Minimal staffing due to COVID-19.
February 1, 4, 2021, BOD5, CBOD, T/X: Dilution water blank failure.
February 1, 8, 10, 15, 22, 2021, Cl: Sample MS/MSD recovery failed but LCS passed.
February 3, 2021, SS, VSS, TS, VTS, T/X: Samlple discarded before analysis could take place.
February 8, 2021, F: Sample MS/MSD recovery failed but LCS passed.
February, 11, 12, 2021, MULTPLE TESTS, T/X: Holiday.
February, 11, 12, 2021, pH, T/X: Sampling error.
February, 13, 14, 2021, MULTPLE TESTS, T/X: Sample holding time exceeded.
February 13-24, 2021, pH, T/X: pH probe out of service.
February 15, 18, 2021, BOD5, T/X: None of the dilutions met acceptance criteria.
February 16, 2021, CR6+, T/X: LCS failure.
February 17, 2021, TS, VTS, T/X: Thermal preservation compromised.
February 20, 2021, SS, VSS, T/X: Residual wright less than 2.5 mg.
February 2021, ALL OTHER BOD5, CBOD: Minimal staffing due to COVID-19.
March 1, 25, 2021, BOD5, CBOD, T/X: LCS failure.
March 2, 2021, S/X: Sample cancelled per M&O.
March 8, 2021, FOG, CN, CR6+, T/X: No chain of custody.
March 15, 2021, F: Sample MS/MSD recovery failed but LCS passed.
March 21, 23, 2021, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
March 29, 2021, CR6+, T/X: Sample analyzed on a different date.
March 29, 2021, Cl: Sample MS/MSD recovery failed but LCS passed.
March 2021, ALL OTHER BOD5, CBOD, T/X: Minimal staffing due to COVID-19.
January-March 2021, Hg, T/X: Digestion thermometer not calibrated.
April 1, 18, 25, 28, 2021, NO2+NO3: Sample MS recovery failed but LCS passed.
April 6, 2021, Hg, T/X: Field blank failure.
April 12, 2021, FOG, T/X: LCS failure.
April 2021, ALL OTHER BOD5, CBOD, T/X: Minimal staffing due to COVID-19.
May 7, 21, 2021, NO2+NO3: Sample MS recovery failed but LCS passed.
May 20, 24, 2021, BOD5, CBOD, T/X: Incubator malfunction.
May 25, 2021, ALL TESTS, S/X: Process or sampling point out of service.
May 25, 2021, Hg, T/X: Field blank failure.
May 28, 29, 30, 31, 2021, ALL TESTS, T/X: Non representative sample, cancelled per M&O.
May 31, 2021, CN, T/X: Sample not chemically preserved in time.
May 31, 2021 FECAL COL, T/X: Holiday, sampled next day.
May 2021, ALL OTHER BOD5, CBOD, T/X: Minimal staffing due to COVID-19.
January-May 27, 2021, TKN, P-TOT, T/X: Minimal staffing due to COVID-19.
June 1, 2021, BOD5, CBOD, T/X: Sample discarded before analyses could be done.
June 1, 6, 13, 20, 2021, NO2+NO3: Sample MS recovery failed but LCS passed.
June 4, 5, 11, 12, 2021, TKN, TOT-PHOS, NH3, NO2+NO3, T/X: Sample holding time exceeded.
June 20, 2021, NH3: Sample MS recovery failed but LCS passed.
July 4, 2021, BOD5, CBOD, TKN , NH3, NO2+NO3, TOT-P, T/X: Delivered outside holding time.
July 5, 2021 FECAL COL, T/X: Holiday, sampled next day.
July 6, 2021, Cr6+, T/X: Sample analyzed on a different date.
July 7, 2021, TKN, T/X: NO2+NO3 > 10 * TKN.
July 8, 2021, Cr6+: Sample MS recovery failed but LCS passed.
July 15, 19, 2021, NO2+NO3: Sample MS recovery failed but LCS passed.
July 23, 24, 2021, SS, VSS, TS, VTS, S/X: Sample was not received in the LIMS.
July 26, 27, 2021, TKN, P-TOT, T/X: Thermal preservation compromised.
August 8, 2021, BOD5, CBOD, T/X: LCS failure.
August 11, 12, 2021, TKN: Sample MS recovery failed but LCS passed.
August 19, 29, 31, 2021, TKN, T/X: NO2+NO3 > 10 * TKN.
August 29, 2021, BOD5, CBOD, T/X: Final DO were not analyzed.
August 30, 31, 2021, BOD5, CBOD, T/X: Expired phosphate buffer used.
September 1, 2, 2021, BOD5, CBOD, T/X: Expired phosphate buffer used.
September 1, 2021, TKN, P-TOT: Sample MS recovery failed but LCS passed.
September 5, 2021, BOD5, CBOD, T/X: Sample not analyzed within holding time.
September 5, 2021, TKN, NH3, NO2+NO3, P-TOT, T/X: Sample was not chemically preserved.
September 13, 14, 15, 16, 2021, BOD5, CBOD, T/X: Blank failure.
September 21, 2021, TKN: Sample MS recovery failed but LCS passed.
November 3, 4, 2021, BOD5, CBOD, T/X: LCS failure.
November 3, 2021, NO2+NO3: Sample MS recovery failed but LCS passed.
November 10, 24, 2021, TKN, NH3, NO2+NO3, TOT P, T/X: Sample was not preserved.
November 11, 2021, NH3, NO2+NO3: Sample MS recovery failed but LCS passed.
November 17, 2021, Multiple tests, S/X: Sample point out of service for maintenance.
November 22, 23, 2021, BOD5, CBOD, T/X: Incubator malfunction, temperature out of range.
November 28, 2021, TKN: Sample MS recovery failed but LCS passed.
November 30, 2021, Pb: Sample MS recovery failed but LCS passed.
December 1, 2, 22, 2021, BOD5, CBOD, T/X: Blank failure.
December 1, 2021, TKN: Sample MS recovery failed but LCS passed.
December 5, 13, 2021, NH3, NO2+NO3: Residual chlorine present in sample.
December 12, 2021, P-TOT: Sample MS recovery failed but LCS passed.
December 15, 2021, Multiple tests, S/X: Sample point out of service for maintenance.
December 16, 2021, BOD5, CBOD, T/X: LCS failure.
December 23, 30, 2021, BOD5, CBOD, TKN, NH3, NO2+NO3, TOT P, T/X: Sample not received in time for preservation.
December 27, 28, 2021, BOD5, CBOD, T/X: Lab error, final reading wasn't observed on fifth day of test.

## Lemont Outfall 2022
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2022-01-01 | 2.92 | 7.4 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1126 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 368.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-02 | 2.84 | 7.2 | 8 | N/S | N/S | N/S | <4 | <4 | 1526 | 162 | 1 | <0.3 | 13.71 | 2.34 | N/S | N/S | 661.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-03 | 2.65 | 7.2 | 8.2 | T/X | T/X | <5 | <4 | <4 | 1520 | 150 | 1 | <0.3 | 15.08 | 2.36 | 0.007 | <5 | 586.65 | 0.7 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-01-04 | 2.48 | 7.3 | 8.2 | T/X | T/X | N/S | <4 | <4 | 1322 | 130 | 1 | <0.3 | 16.02 | 2.37 | N/S | N/S | 451.03 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.007 | 0.06 | 0.05 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 95.23 | 34.88 | 381 | 0.9 | N/S
2022-01-05 | 2.4 | 7.3 | 8 | T/X | T/X | N/S | <4 | <4 | 1208 | 136 | 1 | <0.3 | 17.15 | 2.37 | N/S | N/S | 395.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-06 | 2.33 | 7.4 | 8.4 | T/X | T/X | N/S | <4 | <4 | 1284 | 140 | 1 | <0.3 | 17.91 | 2.32 | N/S | N/S | 414.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-07 | 2.27 | 7.3 | 8.5 | N/S | N/S | N/S | 6 | 5 | 1292 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 422.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-08 | 2.36 | 7.1 | 7.9 | N/S | N/S | N/S | 6 | 5 | 1262 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | 402.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-09 | 2.41 | 7.1 | 7.7 | N/S | N/S | N/S | 14 | 12 | 1354 | 152 | 2 | 0.4 | 17.99 | 2.94 | N/S | N/S | 439.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-10 | 2.21 | 7.2 | 8.4 | T/X | T/X | <5 | 22 | 22 | 1274 | 146 | 3 | <0.3 | 18.7 | 3.41 | <0.005 | <5 | 392.88 | 0.9 | 2100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-01-11 | 2.01 | 7.2 | 8.4 | T/X | T/X | N/S | 8 | 8 | 1226 | 142 | 2 | <0.3 | 19.51 | 3.23 | N/S | N/S | 398.23 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.01 | 0.08 | N/S | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | 89.63 | 31.06 | 352 | 1.2 | N/S
2022-01-12 | 2.24 | 7.2 | 8.1 | 9 | 3 | N/S | 6 | 5 | 1218 | 132 | 2 | <0.3 | 21.55 | 3.26 | N/S | N/S | 400.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-13 | 2.2 | 7.2 | 7.9 | 7 | 3 | N/S | 5 | 4 | 1202 | 136 | <1 | <0.3 | 20.97 | 3.29 | N/S | N/S | 386.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-14 | 2.43 | 7.2 | 8 | N/S | N/S | N/S | 29 | 24 | 1238 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | 401.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-15 | 2.2 | 7.2 | 8 | N/S | N/S | N/S | 10 | 10 | 1360 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | 475.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-16 | 2.21 | 7.3 | 7.1 | N/S | N/S | N/S | 11 | 10 | 1368 | 186 | T/X | T/X | T/X | T/X | N/S | N/S | 488.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-17 | 2.18 | 7.1 | 7.3 | T/X | T/X | <5 | 17 | 15 | 1290 | 154 | 2 | <0.3 | 19.82 | 3.08 | <0.005 | <5 | 442.89 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-18 | 2.18 | 7.2 | 7.8 | T/X | T/X | N/S | 13 | 11 | 1260 | 160 | <1 | 0.3 | 19.96 | 3.04 | N/S | N/S | 422.03 | N/S | 6800 | <0.002 | 0.042 | <0.002 | <0.004 | 0.011 | 0.11 | N/S | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.037 | <0.002 | <0.002 | <0.002 | <3 | 88.77 | 31.44 | 351 | 1.1 | N/S
2022-01-19 | 2.21 | 7.2 | 7.5 | 9 | 5 | N/S | 9 | 8 | 1288 | 174 | 2 | 0.4 | 20.65 | 3.04 | N/S | N/S | 436.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-20 | 2.18 | 7.2 | 8.2 | 12 | 6 | N/S | 13 | 11 | 1292 | 144 | 2 | <0.3 | 23.23 | 2.93 | N/S | N/S | 425.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-21 | 2.18 | 7.1 | 8.4 | N/S | N/S | N/S | 5 | 5 | 1260 | 200 | N/S | N/S | N/S | N/S | N/S | N/S | 418.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-22 | 2.12 | 7.1 | 8 | N/S | N/S | N/S | 4 | 4 | 1268 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | 411.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-23 | 2.16 | 7 | 7.6 | N/S | N/S | N/S | 8 | 7 | 1286 | 218 | 2 | <0.3 | 24.58 | 3.18 | N/S | N/S | 426.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-24 | 2.16 | 7.2 | 7.5 | 9 | 5 | <5 | 9 | 6 | 1376 | 234 | 2 | <0.3 | 23.35 | 3.13 | <0.005 | <5 | 456.51 | 1 | 3800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-01-25 | 2.12 | 7.1 | 7.9 | 7 | 4 | N/S | 5 | 5 | 1434 | 142 | 2 | <0.3 | 24.4 | 3.08 | N/S | N/S | 513.07 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.01 | 0.08 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.037 | <0.002 | <0.002 | <0.002 | N/S | 93.52 | 30.8 | 360 | 0.8 | N/S
2022-01-26 | 2.2 | 7.3 | 7.6 | 6 | 3 | N/S | 6 | 5 | 1360 | 146 | 2 | <0.3 | 24.93 | 3.13 | N/S | N/S | 482.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-27 | 2.05 | 7.2 | 7.7 | 6 | 3 | N/S | 5 | 4 | 1304 | 156 | <1 | <0.3 | 23.94 | 3.28 | N/S | N/S | 435.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-28 | 1.99 | 7.2 | 7.4 | N/S | N/S | N/S | 4 | 4 | 1278 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | 437.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-29 | 2.79 | 7.3 | 7 | N/S | N/S | N/S | 6 | 5 | 1296 | 112 | N/S | N/S | N/S | N/S | N/S | N/S | 454.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-30 | 2.25 | 7.2 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1296 | 88 | 5 | 3 | 16.44 | 3.59 | N/S | N/S | 462.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-31 | 1.96 | 7.2 | 7.6 | T/X | T/X | <5 | <4 | <4 | 1300 | 124 | 2 | 0.3 | 19.13 | 3.16 | <0.005 | 8 | 427.19 | 1 | 5500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-02-01 | 2.34 | 7.2 | 8.1 | T/X | T/X | N/S | <4 | <4 | 1514 | 120 | 2 | <0.3 | 19.41 | 3.21 | N/S | N/S | 587.71 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.008 | 0.07 | 0.05 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 96.1 | 29.78 | 363 | 1 | N/S
2022-02-02 | 2.6 | 7 | 6.1 | 11 | 7 | N/S | 9 | 9 | 1994 | 218 | 2 | <0.3 | 17.98 | 2.86 | N/S | N/S | 855.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-03 | 2.2 | 7.2 | 8.9 | 12 | 9 | N/S | 9 | 7 | 1890 | 204 | 2 | <0.3 | 19.38 | 2.85 | N/S | N/S | 787.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-04 | 2.09 | 7.2 | 8.9 | N/S | N/S | N/S | 9 | 8 | 1712 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 692.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-05 | 2.22 | 7 | 7.5 | N/S | N/S | N/S | 11 | 10 | 1590 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | 627.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-06 | 2.22 | 7.1 | 7.5 | N/S | N/S | N/S | 13 | 11 | 1470 | 122 | 3 | 1.3 | 16.3 | 3.15 | N/S | N/S | 575.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-07 | 2.09 | 7.3 | 8.1 | T/X | T/X | <5 | 11 | 10 | 1470 | 154 | 3 | 0.5 | 17.02 | 3.19 | <0.005 | <5 | 636.81 | 0.9 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-02-08 | 2.14 | 7.3 | 8 | T/X | T/X | N/S | 11 | 10 | 1434 | 172 | 2 | <0.3 | 17.06 | 3.28 | N/S | N/S | 657.03 | N/S | N/S | <0.002 | 0.05 | <0.002 | <0.004 | 0.011 | 0.12 | N/S | <0.002 | 0.027 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 106.96 | 34.27 | 408 | 0.7 | N/S
2022-02-09 | 2.23 | 7.2 | 7.9 | T/X | T/X | N/S | 6 | 5 | 1434 | 140 | 2 | 0.6 | 18.41 | 3.31 | N/S | N/S | 555.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-10 | 2.2 | 7.5 | 4.9 | T/X | T/X | N/S | 15 | 12 | 1728 | 186 | T/X | T/X | T/X | T/X | N/S | N/S | 712.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-11 | 2.7 | 7.4 | 7.1 | N/S | N/S | N/S | 8 | 6 | 1974 | 200 | N/S | N/S | N/S | N/S | N/S | N/S | 893.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-12 | 3.25 | 7.1 | 7.8 | N/S | N/S | N/S | 8 | 5 | 2100 | 236 | N/S | N/S | N/S | N/S | N/S | N/S | 990.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-13 | 3.04 | 7.2 | 7.1 | N/S | N/S | N/S | 7 | 5 | 1854 | 224 | 2 | 0.7 | 15.24 | 2.06 | N/S | N/S | 818.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-14 | 2.34 | 7.2 | 8.2 | 18 | 15 | <5 | 5 | 4 | 1652 | 192 | 2 | 0.3 | 17.89 | 2.23 | <0.005 | <5 | 699.32 | 0.8 | 5500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-02-15 | 2.23 | 7.2 | 8.5 | 17 | 15 | N/S | 11 | 9 | 1468 | 138 | 2 | <0.3 | 20.69 | 2.59 | N/S | N/S | 646.61 | N/S | N/S | <0.002 | 0.052 | <0.002 | <0.004 | 0.008 | 0.12 | N/S | <0.002 | 0.027 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 96.86 | 33.45 | 380 | 1.1 | N/S
2022-02-16 | 2.86 | 7.2 | 7.9 | 13 | 8 | N/S | 12 | 11 | 1374 | 144 | 2 | <0.3 | 18.15 | 2.72 | N/S | N/S | 583.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-17 | 4.14 | 6.9 | 8.4 | 24 | 9 | N/S | 26 | 22 | 1126 | 156 | 2 | <0.3 | 9.74 | 1.45 | N/S | N/S | 468.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-18 | 4.1 | 7 | 8.5 | N/S | N/S | N/S | 16 | 11 | 1246 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | 517.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-19 | 4.1 | 7 | 7.6 | N/S | N/S | N/S | 14 | 9 | 1324 | 110 | N/S | N/S | N/S | N/S | N/S | N/S | 564.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-20 | 4.1 | 7 | 7.4 | N/S | N/S | N/S | 15 | 11 | 1392 | 96 | T/X | T/X | T/X | T/X | N/S | N/S | 592.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-21 | 4.1 | 7 | 7.2 | 23 | 16 | <5 | 17 | 14 | 1514 | 144 | <4 | 0.5 | 11.19 | 1.59 | <0.005 | <5 | 696.99 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-22 | 4.1 | 7.2 | 8.1 | 13 | 8 | N/S | 17 | 14 | 1356 | 134 | 2 | <0.3 | 9.4 | 1.3 | N/S | N/S | 578.16 | N/S | 4500 | <0.002 | 0.046 | <0.002 | <0.004 | 0.009 | 0.12 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | <3 | 90.03 | 31.8 | 356 | 1.4 | N/S
2022-02-23 | 4.1 | 7.1 | 8.9 | 11 | 5 | N/S | 9 | 7 | 1090 | 138 | 1 | <0.3 | 9.69 | 1.01 | N/S | N/S | 472.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-24 | 4.1 | 7.1 | 9.1 | 9 | 5 | N/S | 11 | 12 | 1140 | 118 | <4 | <0.3 | 11.95 | 1.1 | N/S | N/S | 466.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-25 | 4.1 | 7.3 | 8.4 | N/S | N/S | N/S | 5 | <4 | 1228 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 487.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-26 | 4.1 | 7.3 | 7.4 | N/S | N/S | N/S | 7 | 4 | 1242 | 112 | N/S | N/S | N/S | N/S | N/S | N/S | 493.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-27 | 4.1 | 7.3 | 7.4 | N/S | N/S | N/S | 8 | <4 | 1170 | 82 | <4 | <0.3 | 13.34 | 1.59 | N/S | N/S | 468.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-28 | 4.1 | 7.2 | 7.7 | 4 | <2 | N/S | <4 | <4 | 1156 | 94 | <4 | <0.3 | 12.89 | 1.47 | <0.005 | <5 | 478.15 | 0.6 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-03-01 | 4.1 | 7.3 | 8.3 | 9 | 4 | T/X | 10 | 8 | 1246 | 144 | 2 | <0.3 | 13.95 | 1.7 | N/S | N/S | 482.54 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.007 | 0.09 | 0.04 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 90.94 | 32.98 | 363 | <0.5 | N/S
2022-03-02 | 4.1 | 7.2 | 7.6 | 9 | 5 | N/S | 8 | 7 | 1284 | 120 | <4 | <0.3 | 15.07 | 1.77 | N/S | N/S | 480.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-03 | 3.63 | 7.3 | 7.8 | 11 | 6 | N/S | 8 | 7 | 1338 | 128 | 2 | 0.3 | 15.04 | 2.12 | N/S | N/S | 497.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-04 | 2.84 | 7.4 | 8.1 | N/S | N/S | <5 | 5 | 5 | 1312 | 168 | N/S | N/S | N/S | N/S | N/S | N/S | 455.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-05 | 2.74 | 7.1 | 8.2 | N/S | N/S | N/S | 5 | 4 | 1282 | 140 | N/S | N/S | N/S | N/S | N/S | N/S | 448.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-06 | 3.16 | 7.3 | 7.9 | N/S | N/S | N/S | 7 | 5 | 1390 | 166 | <4 | <0.3 | 17.31 | 2.36 | N/S | N/S | 531.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-07 | 3.74 | 7.3 | 8.3 | 7 | 4 | <5 | 8 | 7 | 1572 | 174 | 1 | <0.3 | 14.04 | 1.9 | 0.007 | <5 | 793.58 | 0.6 | 500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-03-08 | 4.1 | 7.4 | 8.6 | 8 | 5 | N/S | 8 | 7 | 1462 | 150 | 1 | <0.3 | 11.25 | 1.39 | N/S | N/S | 628.47 | N/S | N/S | <0.002 | 0.05 | <0.002 | <0.004 | 0.014 | 0.09 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 96.55 | 35.45 | 387 | 2.2 | N/S
2022-03-09 | 4.1 | 7.4 | 8.3 | 9 | 5 | N/S | 8 | 7 | 1350 | 168 | <4 | <0.3 | 12.41 | 1.59 | N/S | N/S | 518.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-10 | 3.82 | 7.3 | 8 | 10 | 5 | N/S | 8 | 7 | 1338 | 182 | <4 | <0.3 | 12.79 | 1.65 | N/S | N/S | 494.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-11 | 3.01 | 7.5 | 8.3 | N/S | N/S | N/S | 6 | 4 | 1426 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | 537.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-12 | 3.05 | 7.4 | 8 | N/S | N/S | N/S | 7 | 4 | 1432 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | 533.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-13 | 2.74 | 7.4 | 7.9 | N/S | N/S | N/S | 7 | 4 | 1266 | 140 | <4 | 0.4 | 15.45 | 2.04 | N/S | N/S | 528.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-14 | 2.7 | 7.3 | 8.2 | T/X | T/X | <5 | 4 | <4 | 1242 | 134 | <4 | 0.4 | 14.85 | 2.31 | <0.005 | <5 | 456.22 | 0.8 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-03-15 | 2.06 | 7.5 | 8.3 | T/X | T/X | N/S | 10 | 8 | 1204 | 92 | 2 | 0.7 | 13.07 | 2.42 | N/S | N/S | 440.95 | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.007 | 0.09 | N/S | <0.002 | 0.074 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | 91.58 | 33.19 | 365 | 0.6 | N/S
2022-03-16 | 2.4 | 7.4 | 7.7 | T/X | T/X | N/S | 8 | 7 | 1216 | 106 | 3 | 1.7 | 11.07 | 2.65 | N/S | N/S | 421.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-17 | 2.81 | 7.4 | 7.2 | T/X | T/X | N/S | 8 | 6 | 1226 | 128 | 4 | 2.1 | 10.78 | 2.74 | N/S | N/S | 412.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-18 | 2.66 | 7.5 | 8.3 | N/S | N/S | N/S | 11 | 9 | 1246 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | 407.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-19 | 4.1 | 7.2 | 7.7 | N/S | N/S | N/S | 23 | 19 | 1292 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | 476.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-20 | 4.1 | 7.2 | 7.1 | N/S | N/S | N/S | 23 | 20 | 1250 | 174 | 2 | <0.3 | 9.84 | 1.46 | N/S | N/S | 444.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-21 | 3.94 | 7.3 | 8 | T/X | T/X | T/X | 12 | 10 | 1224 | 186 | 2 | <0.3 | 11.17 | 1.45 | <0.005 | <5 | 406.59 | 0.6 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-03-22 | 3.94 | 7.3 | 8.2 | T/X | T/X | N/S | 7 | 6 | 1146 | 122 | 1 | <0.3 | 12.62 | 1.49 | N/S | N/S | 373.66 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.011 | 0.09 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | 88.12 | 34.49 | 362 | 0.7 | N/S
2022-03-23 | 4.1 | 7.4 | 8 | T/X | T/X | N/S | 10 | 8 | 1142 | 150 | 1 | <0.3 | 11.83 | 1.43 | N/S | N/S | 388.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-24 | 4.1 | 7.3 | 7.9 | T/X | T/X | N/S | 5 | 4 | 1070 | 138 | 2 | <0.3 | 11.3 | 1.51 | N/S | N/S | 353.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-25 | 4.1 | 7.3 | 8.3 | N/S | N/S | N/S | 6 | 4 | 1080 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | 364.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-26 | 3.48 | 7.4 | 6.9 | N/S | N/S | N/S | 4 | <4 | 1150 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | 380.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-27 | 2.72 | 7.6 | 7.1 | N/S | N/S | N/S | 5 | <4 | 1154 | 110 | <4 | <0.3 | 11.89 | 1.67 | N/S | N/S | 379.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-28 | 1.43 | 7.6 | 7.7 | 5 | <2 | <5 | 6 | 5 | 1122 | 138 | <4 | <0.3 | 15.81 | 2.25 | <0.005 | <5 | 357.91 | 0.6 | 1100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-03-29 | 3.49 | 7.6 | 8.7 | 16 | 7 | N/S | 14 | 12 | 1082 | 128 | 3 | 1.4 | 14.55 | 2.23 | N/S | N/S | 337.29 | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.01 | 0.15 | N/S | <0.002 | 0.03 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 94.8 | 36.05 | 385 | 1 | N/S
2022-03-30 | 3.96 | 7.5 | 7.1 | 15 | 6 | N/S | 13 | 10 | 992 | 124 | 3 | 2 | 10.15 | 1.64 | N/S | N/S | 304.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-31 | 4.03 | 7.3 | 8.1 | 7 | 4 | N/S | 9 | 7 | 708 | 94 | 1 | <0.3 | 7.17 | 0.85 | N/S | N/S | 219.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-01 | 4.08 | 7.5 | 9 | N/S | N/S | N/S | 9 | 7 | 822 | 138 | N/S | N/S | N/S | N/S | N/S | N/S | 242.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-02 | 4.09 | 7.4 | 8.1 | N/S | N/S | N/S | 8 | 7 | 886 | 138 | N/S | N/S | N/S | N/S | N/S | N/S | 252.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-03 | 4.1 | 7.5 | 7.9 | N/S | N/S | N/S | 10 | 8 | 910 | 142 | 1 | <0.3 | 9.22 | 1.13 | N/S | N/S | 266.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-04 | 4.09 | 7.4 | 7.5 | 7 | 4 | <5 | 9 | 7 | 914 | 116 | 2 | <0.3 | 10.17 | 1.5 | <0.005 | <5 | 290.48 | 0.5 | 8100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-04-05 | 4.08 | 7.5 | 8.5 | 5 | 3 | N/S | 6 | <4 | 948 | 136 | 1 | <0.3 | 9.95 | 1.13 | N/S | N/S | 296.86 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.008 | 0.08 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 82.26 | 31.86 | 337 | 1.4 | N/S
2022-04-06 | 4.07 | 7.6 | 6.4 | 5 | 3 | N/S | 6 | 5 | 850 | 146 | 1 | <0.3 | 11.05 | 1.24 | N/S | N/S | 273.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-07 | 4.05 | 7.4 | 8.1 | 5 | 3 | N/S | 7 | 5 | 794 | 134 | 1 | <0.3 | 10.02 | 1.12 | N/S | N/S | 242.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-08 | 4.06 | 7.4 | 8 | N/S | N/S | N/S | 5 | 5 | 884 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | 271.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-09 | 4.04 | 7.5 | 7.7 | N/S | N/S | N/S | <4 | <4 | 950 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 296.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-10 | 4.01 | 7.6 | 7.5 | N/S | N/S | N/S | <4 | <4 | 954 | 142 | <4 | <0.3 | 11.24 | 1.27 | N/S | N/S | 296.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-11 | 4.01 | 7.5 | 8 | 6 | 3 | <5 | 5 | 4 | 916 | 160 | 1 | <0.3 | 11.56 | 1.3 | <0.005 | <5 | 300.29 | 0.6 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-04-12 | 4.01 | 7.6 | 8.7 | 4 | 2 | N/S | 4 | <4 | 942 | 126 | <4 | <0.3 | 12.66 | 1.25 | N/S | N/S | 301.41 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 84.78 | 33.19 | 348 | 1 | N/S
2022-04-13 | 4 | 7.5 | 8.3 | 5 | 3 | N/S | <4 | <4 | 950 | 162 | <4 | <0.3 | 14.53 | 1.76 | N/S | N/S | 303.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-14 | 4.02 | 7.5 | 8.2 | 4 | 2 | N/S | <4 | <4 | 874 | 182 | 1 | <0.3 | 12.91 | 1.49 | N/S | N/S | 257.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-15 | 4.04 | 7.6 | 8.4 | N/S | N/S | N/S | <4 | <4 | 926 | 114 | N/S | N/S | N/S | N/S | N/S | N/S | 277.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-16 | 4.03 | 7.5 | 7.8 | N/S | N/S | N/S | <4 | <4 | 962 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | 301.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-17 | 3.74 | 7.5 | 7.1 | N/S | N/S | N/S | 4 | 4 | 1046 | 134 | 3 | 1.5 | 12.24 | 2.31 | N/S | N/S | 322.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-18 | 2.87 | 7.4 | 7.2 | 9 | 6 | <5 | <4 | 6 | 1126 | 168 | 2 | <0.3 | 12.89 | 1.99 | <0.005 | <5 | 343.55 | 0.7 | 140000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-04-19 | 2.92 | 8.1 | 7.7 | 7 | 4 | N/S | 5 | 5 | 1118 | 186 | 2 | <0.3 | 16.04 | 2.06 | N/S | N/S | 337.9 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.008 | 0.07 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 95.22 | 35.22 | 383 | 10.7 | N/S
2022-04-20 | 2.57 | 7.7 | 8.3 | 7 | 4 | N/S | 4 | 4 | 1126 | 176 | 2 | <0.3 | 17.33 | 2.36 | N/S | N/S | 334.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-21 | 3.15 | 7.5 | 7.5 | 7 | 4 | N/S | 8 | 7 | 958 | 148 | <4 | <0.3 | 14.03 | 2.07 | N/S | N/S | 292.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-22 | 3.6 | 7.5 | 8.2 | N/S | N/S | N/S | 10 | 7 | 962 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | 294.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-23 | 3.73 | 7.6 | 8.3 | N/S | N/S | N/S | 9 | 7 | 814 | 134 | N/S | N/S | N/S | N/S | N/S | N/S | 253.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-24 | 3.75 | 7.6 | 7.3 | N/S | N/S | N/S | 10 | 7 | 898 | 142 | 2 | <0.3 | 11.28 | 1.52 | N/S | N/S | 268.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-25 | 3.9 | 7.5 | 7.9 | 11 | 7 | <5 | 11 | 11 | 970 | 148 | 2 | <0.3 | 12.12 | 1.59 | <0.005 | <5 | 277.58 | 0.5 | 3500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-04-26 | 3.47 | 7.6 | 7.7 | 12 | 8 | N/S | 9 | 7 | 984 | 138 | 2 | <0.3 | 12.28 | 1.61 | N/S | N/S | 281.26 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.011 | 0.15 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | 88.15 | 33.17 | 357 | 1.8 | N/S
2022-04-27 | 1.82 | 7.6 | 7.9 | 14 | 8 | N/S | 10 | 8 | 984 | 154 | 2 | <0.3 | 13.8 | 2.01 | N/S | N/S | 265.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-28 | 3.71 | 7.3 | 8.8 | 21 | 10 | N/S | 11 | 9 | 994 | 150 | 5 | 3 | 13.2 | 2.11 | N/S | N/S | 274.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-29 | 3.53 | 7.3 | 6.9 | N/S | N/S | N/S | 14 | 12 | 1062 | 120 | N/S | N/S | N/S | N/S | N/S | N/S | 294.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-30 | 2.68 | 7.4 | 7.2 | N/S | N/S | N/S | 11 | 9 | 1064 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 305.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-01 | 3.31 | 7.2 | 8.3 | N/S | N/S | N/S | 14 | 12 | 998 | 174 | 3 | <0.3 | 13.67 | 2.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-02 | 3.07 | 7.1 | 7.6 | T/X | T/X | <5 | 20 | 16 | 1032 | 152 | 3 | <0.3 | 15.45 | 2.26 | 0.005 | <5 | 296.95 | 0.6 | 67000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-05-03 | 3.5 | 7.4 | 7.5 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | 2.6 | S/X
2022-05-04 | 3.78 | 7.3 | 8.4 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X
2022-05-05 | 3.48 | 7.4 | 8 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X
2022-05-06 | 4.01 | 7.4 | 8.1 | N/S | N/S | N/S | 12 | 9 | 868 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-07 | 4.01 | 7.4 | 8.3 | N/S | N/S | N/S | 6 | <4 | 838 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-08 | 4.01 | 7.5 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1002 | 182 | 2 | <0.3 | 10.02 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-09 | 3.38 | 7.4 | 8.3 | 9 | 5 | <5 | 6 | 4 | 1014 | 156 | 1 | 0.4 | 10.4 | 1.33 | <0.005 | <5 | 276.84 | 0.6 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-05-10 | 4 | 7.4 | 7.5 | 6 | 3 | N/S | 4 | <4 | 1024 | 146 | 1 | <0.3 | 11.05 | 1.34 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.008 | 0.07 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | N/S | 93.68 | 34.94 | 378 | 2.9 | N/S
2022-05-11 | 4.01 | 7.3 | 7.7 | T/X | T/X | N/S | 14 | 12 | 1058 | 166 | 2 | 1.2 | 11.03 | 1.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-12 | 3.26 | 7.3 | 7.2 | T/X | T/X | N/S | 10 | 8 | 1162 | 174 | 2 | 1 | 12.34 | 1.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-13 | 2.89 | 7.4 | 8.2 | N/S | N/S | N/S | 7 | 8 | 1186 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-14 | 2.86 | 7.4 | 8.1 | N/S | N/S | N/S | 9 | 8 | 1156 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-15 | 3.01 | 7.2 | 7.1 | N/S | N/S | N/S | 11 | 9 | 1218 | 192 | 2 | <0.3 | 15.04 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-16 | 2.57 | 7.4 | 7.4 | 24 | 13 | <5 | 10 | 9 | 1270 | 212 | 2 | <0.3 | 14.28 | 2.19 | <0.005 | <5 | 379.6 | 0.8 | 21000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-05-17 | 2.19 | 7.4 | 8 | 11 | 7 | N/S | 12 | 10 | 1312 | 246 | 2 | 0.9 | 15.29 | 2 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.01 | 0.12 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | 102.48 | 35.14 | 401 | 0.8 | N/S
2022-05-18 | 2.56 | 7.4 | 8.4 | T/X | T/X | N/S | 10 | 8 | 1188 | 212 | <4 | <0.3 | 15.81 | 1.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-19 | 2.34 | 7.4 | 8 | T/X | T/X | N/S | 11 | 9 | 1078 | 176 | <4 | <0.3 | 15.87 | 1.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-20 | 2.29 | 7.4 | 7.9 | N/S | N/S | N/S | 5 | 5 | 1230 | 188 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-21 | 3.55 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 4 | 980 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-22 | 3.43 | 7.3 | 7.6 | N/S | N/S | N/S | 5 | <4 | 1006 | 124 | <4 | <0.3 | 11.91 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-23 | 3.02 | 7.4 | 8.4 | 6 | 3 | <5 | 4 | <4 | 1198 | 190 | 2 | 0.6 | 12.24 | 2 | <0.005 | <5 | 347.05 | 0.7 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-05-24 | 2.4 | 7.5 | 9 | 4 | 3 | N/S | 4 | <4 | 1200 | 152 | <4 | <0.3 | 14.87 | 2.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.009 | 0.07 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 99.96 | 35.07 | 394 | 1.3 | N/S
2022-05-25 | 2.52 | 7.5 | 8.7 | T/X | T/X | N/S | 5 | <4 | 1166 | 128 | <4 | <0.3 | 17.1 | 2.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-26 | 2.87 | 7.5 | 8.5 | T/X | T/X | N/S | 11 | 9 | 1026 | 106 | <4 | <0.3 | 15.17 | 2.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-27 | 3.04 | 7.4 | 8.3 | N/S | N/S | N/S | 8 | 6 | 1018 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-28 | 3.05 | 7.4 | 8.4 | N/S | N/S | N/S | 9 | 6 | 1068 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-29 | 2.76 | 7.3 | 8 | N/S | N/S | N/S | 10 | 8 | 1180 | 184 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-30 | 2.37 | 7.4 | 8.1 | T/X | T/X | <5 | 8 | 7 | 1232 | 218 | <4 | 0.3 | 16.72 | 2.54 | N/S | <5 | 389.8 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-31 | 2.35 | 7.4 | 8.2 | T/X | T/X | N/S | 7 | 5 | 1228 | 196 | <4 | <0.3 | 17.07 | 2.59 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.011 | 0.13 | 0.06 | <0.002 | 0.019 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | <3 | 104.99 | 35.03 | 406 | 1.6 | N/S
2022-06-01 | 2.21 | 7.4 | 8.2 | 9 | 4 | N/S | 9 | 6 | 1246 | 162 | <4 | <0.3 | 18.11 | 3.05 | <0.005 | N/S | N/S | N/S | 900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-02 | 2.16 | 7.4 | 8.4 | 8 | 4 | N/S | 7 | 5 | 1276 | 194 | <4 | <0.3 | 19.7 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-03 | 2.18 | 7.4 | 8.7 | N/S | N/S | N/S | 4 | <4 | 1324 | 204 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-04 | 2.18 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1340 | 222 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-05 | 2.18 | 7.5 | 7.8 | N/S | N/S | N/S | 4 | <4 | 1282 | 202 | 2 | 0.5 | 18.87 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-06 | 2.64 | 7.4 | 8.1 | 7 | 3 | <5 | 4 | <4 | 1252 | 250 | <4 | <0.3 | 17.09 | 2.85 | <0.005 | <5 | 377.93 | 0.8 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-06-07 | 4.14 | 7.2 | 8.2 | 7 | 5 | N/S | 7 | 5 | 1048 | 212 | 1 | <0.3 | 11.11 | 1.74 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.008 | 0.1 | 0.05 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 89.97 | 29.23 | 345 | 1.7 | N/S
2022-06-08 | 4 | 7.3 | 7.9 | 20 | 9 | N/S | 16 | 12 | 974 | 144 | 3 | 0.4 | 10.89 | 1.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-09 | 3.25 | 7.3 | 8.2 | 10 | 4 | N/S | 6 | 5 | 1002 | 140 | 2 | <0.3 | 10.85 | 1.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-10 | 2.68 | 7.4 | 8.2 | N/S | N/S | N/S | 5 | 4 | 1248 | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-11 | 2.49 | 7.4 | 8.3 | N/S | N/S | N/S | 6 | 4 | 1390 | 282 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-12 | 2.55 | 7.4 | 8.3 | N/S | N/S | N/S | 6 | 5 | 1352 | 234 | <4 | <0.3 | 16.32 | 3.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-13 | 2.48 | 7.3 | 8.4 | T/X | T/X | <5 | 6 | 5 | 1386 | 256 | <4 | 0.4 | 16.05 | 2.94 | <0.005 | <5 | 438.14 | 0.8 | 8600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-06-14 | 2.33 | 7.4 | 8.3 | T/X | T/X | N/S | 4 | 4 | 1328 | 226 | <4 | 0.3 | 14.24 | 2.76 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.008 | 0.08 | N/S | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 107.76 | 36.37 | 419 | 0.5 | N/S
2022-06-15 | 2.27 | 7.4 | 8.4 | T/X | T/X | N/S | 8 | 7 | 1496 | 278 | 2 | <0.3 | 16.77 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-16 | 2.32 | 7.4 | 8.4 | T/X | T/X | N/S | 4 | <4 | 1492 | 228 | 2 | 0.5 | 17.53 | 3.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-17 | 2.21 | 7.4 | 8.3 | N/S | N/S | N/S | 6 | 5 | 1448 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-18 | 2.18 | 7.7 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1446 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-19 | 2.1 | 7.6 | 7.4 | N/S | N/S | N/S | 4 | <4 | 1284 | 200 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-20 | 2.15 | 7.6 | 7.3 | 5 | <2 | <5 | 4 | <4 | 1114 | 170 | <4 | <0.3 | 20 | 3.17 | <0.005 | <5 | 307.83 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-21 | 2.28 | 7.4 | 7.9 | 14 | 4 | N/S | 12 | 9 | 1252 | 216 | 3 | 0.9 | 17.55 | 3.49 | N/S | N/S | N/S | N/S | 24000 | <0.002 | 0.042 | <0.002 | <0.004 | 0.008 | 0.11 | N/S | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | <3 | 100.86 | 32.77 | 387 | 0.9 | N/S
2022-06-22 | 2.13 | 7.5 | 7.5 | 4 | 3 | N/S | 5 | 4 | 1452 | 272 | 2 | 0.5 | 15.68 | 3.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-23 | 2.19 | 7.4 | 7.7 | 10 | 7 | N/S | 7 | 5 | 1544 | 234 | 3 | 1.3 | 13.34 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-24 | 2.2 | 7.4 | 7.1 | N/S | N/S | N/S | 5 | 4 | 1616 | 298 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-25 | 2.6 | 7.4 | 7.4 | N/S | N/S | N/S | 5 | 4 | 1454 | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-26 | 2.92 | 7.2 | 7.6 | N/S | N/S | N/S | 4 | <4 | 1212 | 192 | <4 | <0.3 | 16.45 | 2.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-27 | 2.28 | 7.5 | 7.8 | 5 | 3 | <5 | 4 | 4 | 1318 | 256 | <4 | <0.3 | 18.51 | 2.83 | 0.005 | <5 | 415.56 | 0.8 | 990 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-06-28 | 2.02 | 7.4 | 8.1 | 6 | 6 | N/S | 5 | 4 | 1410 | 242 | <4 | 0.5 | 20.88 | 3.47 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.049 | <0.002 | <0.004 | 0.007 | 0.09 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 124.62 | 39.86 | 475 | 1.4 | N/S
2022-06-29 | 1.85 | 7.4 | 6.8 | T/X | T/X | N/S | 7 | 7 | 1312 | 186 | 4 | 2.5 | 18.31 | 3.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-30 | 1.87 | 7.4 | 7.3 | T/X | T/X | N/S | 12 | 10 | 1210 | 106 | 9 | 6.2 | 8.97 | 3.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-01 | 1.46 | 7.4 | 4.4 | N/S | N/S | N/S | <4 | <4 | 1322 | 298 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-02 | 3.08 | 7.3 | 4.8 | N/S | N/S | N/S | 9 | 6 | 1544 | 412 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-03 | 2.91 | 7.3 | 5 | N/S | N/S | N/S | 7 | 5 | 1718 | 418 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-04 | 2.31 | 7.4 | 5 | T/X | T/X | <5 | 7 | 5 | 1576 | 296 | 2 | 1 | 14.74 | 3.07 | <0.005 | <5 | 524.8 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-05 | 2.03 | 7.2 | 5.3 | T/X | T/X | N/S | 9 | 6 | 1328 | 260 | 3 | 1.8 | 11.62 | 2.68 | N/S | N/S | N/S | N/S | 8700 | <0.002 | 0.044 | <0.002 | <0.004 | 0.008 | 0.14 | 0.05 | <0.002 | 0.042 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | <3 | 103.81 | 32.77 | 394 | 0.9 | N/S
2022-07-06 | 3.76 | 7.2 | 3.7 | T/X | T/X | N/S | <4 | <4 | 1264 | 238 | 5 | 3.3 | 13.86 | 2.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-07 | 2.85 | 7.2 | 5.2 | 6 | 4 | N/S | 7 | 6 | 1300 | 190 | <4 | 0.3 | 19.4 | 2.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-08 | 2.19 | 7.3 | 6.1 | N/S | N/S | N/S | <4 | <4 | 1336 | 188 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-09 | 2.19 | 7.6 | 7.9 | N/S | N/S | N/S | 7 | 5 | 1356 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-10 | 2.16 | 7.4 | 7.8 | N/S | N/S | N/S | 11 | 9 | 1452 | 252 | 5 | T/X | T/X | 3.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-11 | 1.49 | 7.5 | 7 | T/X | T/X | <5 | 4 | <4 | 1474 | 248 | 4 | 3.1 | 14.54 | 3.25 | <0.005 | <5 | 472.92 | 0.9 | 230000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-07-12 | 1.86 | 7.4 | 6.4 | T/X | T/X | N/S | 9 | 7 | 1428 | 228 | 6 | 4.2 | 13.39 | 3.56 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.048 | <0.002 | <0.004 | 0.009 | 0.13 | N/S | <0.002 | 0.114 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 119.16 | 39.24 | 459 | 1 | N/S
2022-07-13 | 1.91 | 7.4 | 6.8 | T/X | T/X | N/S | 7 | 6 | 1574 | 308 | 5 | 4.1 | 17.88 | 3.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-14 | 2.83 | 7.3 | 5.3 | T/X | T/X | N/S | 7 | 5 | 1648 | 256 | 3 | 1.9 | 20.82 | 3.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-15 | 2.63 | 7.4 | 8 | N/S | N/S | N/S | 7 | 5 | 1390 | 226 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-16 | 3.8 | 7.3 | 6.8 | N/S | N/S | N/S | 6 | 4 | 1104 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-17 | 2.48 | 7.5 | 7.4 | N/S | N/S | N/S | 6 | 4 | 1184 | 186 | <4 | <0.3 | 18.35 | 2.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-18 | 2.51 | 7.4 | 7.9 | 5 | 3 | <5 | 6 | 5 | 1218 | 182 | <4 | <0.3 | 19.28 | 2.35 | <0.005 | <5 | 382.46 | 0.8 | 16000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-07-19 | 2.25 | 7.4 | 8 | 6 | 4 | N/S | 7 | 6 | 1316 | 208 | 2 | <0.3 | 19.04 | 3.43 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.009 | 0.1 | N/S | <0.002 | 0.022 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 101.67 | 36.46 | 404 | <0.5 | N/S
2022-07-20 | 2.1 | 7.5 | 7.5 | T/X | T/X | N/S | 4 | <4 | 1392 | 206 | 3 | <0.3 | 17.24 | 3.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-21 | 2.09 | 7.5 | 8.1 | T/X | T/X | N/S | 7 | 5 | 1308 | 218 | <4 | 0.4 | 20.45 | 3.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-22 | 2.01 | 7.5 | 7.6 | N/S | N/S | N/S | 7 | 5 | 1320 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-23 | 3.22 | 7.4 | 7.7 | N/S | N/S | N/S | 8 | 6 | 544 | 104 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-24 | 4.1 | 7.2 | 7.4 | N/S | N/S | N/S | 7 | 4 | 778 | 154 | 2 | 0.4 | 8.87 | 1.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-25 | 4.1 | 7.3 | 7.7 | T/X | T/X | <5 | 7 | 5 | 520 | 110 | 2 | <0.3 | 10.89 | 1.51 | <0.005 | <5 | 224.96 | 0.6 | 36000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-07-26 | 4.1 | 7.3 | 7.5 | T/X | T/X | N/S | 8 | 6 | 1110 | 248 | 4 | 1.8 | 12.37 | 2.08 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.008 | 0.13 | N/S | <0.002 | 0.032 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 96.6 | 33.63 | 380 | 1.3 | N/S
2022-07-27 | 2.69 | 7.5 | 7.3 | 6 | 3 | N/S | 6 | 5 | 1198 | 242 | 2 | 0.3 | 17.92 | 2.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-28 | 2.37 | 7.5 | 7.9 | 6 | 6 | N/S | 7 | 6 | 1248 | 270 | 2 | 0.4 | 19.64 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-29 | 2.38 | 7.5 | 6.4 | N/S | N/S | N/S | 12 | 9 | 1278 | 232 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-30 | 2.27 | 7.4 | 6.3 | N/S | N/S | N/S | 10 | 7 | 1436 | 274 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-31 | 2.26 | 7.6 | 6 | N/S | N/S | N/S | 11 | 8 | 1580 | 304 | 6 | 4 | 14.71 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-01 | 2.1 | 7.5 | 7 | 12 | 7 | <5 | 12 | 9 | 1580 | 240 | 8 | 5.6 | 13.9 | 3.23 | <0.005 | <5 | 537.92 | 0.9 | 110000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-08-02 | 2.16 | 7.5 | 7.1 | 11 | 5 | N/S | 10 | 8 | 1514 | 284 | 6 | 3.3 | 17.79 | 3.24 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.051 | <0.002 | <0.004 | 0.011 | 0.14 | 0.09 | <0.002 | 0.026 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | 110.01 | 37.98 | 431 | <0.5 | N/S
2022-08-03 | 2.18 | 7.5 | 6.8 | 9 | 7 | N/S | 13 | 11 | 1470 | 302 | 3 | 1.3 | 21 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-04 | 1.9 | 7.5 | 7.3 | 13 | 7 | N/S | 14 | 11 | 1370 | 268 | 3 | 0.5 | 21.69 | 3.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-05 | 1.99 | 7.4 | 7.1 | N/S | N/S | N/S | 10 | 7 | 1398 | 272 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-06 | 2.01 | 7.4 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1476 | 332 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-07 | 2.25 | 7.4 | 7 | N/S | N/S | N/S | <4 | <4 | 1376 | 294 | 2 | 0.3 | 20.79 | 3.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-08 | 2.61 | 7.4 | 7.4 | T/X | T/X | <5 | 8 | 6 | 1206 | 236 | 2 | <0.3 | 17.15 | 2.66 | <0.005 | <5 | 360.62 | 0.8 | 450000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-08-09 | 2.13 | 7.4 | 7.1 | T/X | T/X | N/S | 4 | 4 | 1218 | 222 | <4 | <0.3 | 19.42 | 2.34 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.009 | 0.09 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 93.49 | 33.49 | 371 | 1.7 | N/S
2022-08-10 | 1.97 | 7.4 | 7.3 | T/X | T/X | N/S | 6 | 6 | 1228 | 218 | <4 | 0.3 | 20.79 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-11 | 2.11 | 7.4 | 7 | T/X | T/X | N/S | 4 | <4 | 1180 | 156 | 2 | <0.3 | 20.92 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-12 | 2.05 | 7.5 | 7.4 | N/S | N/S | N/S | 7 | 5 | 1506 | 468 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-13 | 2.11 | 7.4 | 7.2 | N/S | N/S | N/S | 9 | 8 | 1532 | 448 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-14 | 2.13 | 7.6 | 6.1 | N/S | N/S | N/S | 16 | 14 | 1550 | 470 | <4 | <0.3 | 18.55 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-15 | 2.11 | 7.4 | 7 | T/X | T/X | <5 | 15 | 13 | 1312 | 310 | 2 | 0.3 | 18.41 | 3.66 | <0.005 | <5 | 406.84 | 1 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-08-16 | 2.06 | 7.5 | 7.1 | T/X | T/X | N/S | 9 | 8 | 1368 | 308 | 2 | 0.3 | 19.26 | 3.64 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.011 | 0.14 | N/S | <0.002 | 0.023 | <0.002 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | N/S | 121.25 | 39.7 | 466 | 0.6 | N/S
2022-08-17 | 1.84 | 7.4 | 7 | T/X | T/X | N/S | 7 | 6 | 1316 | 216 | <4 | 0.3 | 22.49 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-18 | 1.88 | 7.4 | 7.5 | T/X | T/X | N/S | 8 | 6 | 1490 | 348 | <4 | 0.3 | 24.54 | 3.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-19 | 1.86 | 7.5 | 7.3 | N/S | N/S | N/S | 6 | 6 | 1482 | 332 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-20 | 3.06 | 7.4 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1104 | 238 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-21 | 3.86 | 7.3 | 7.2 | N/S | N/S | N/S | 5 | 4 | 966 | 182 | 1 | 0.4 | 11.02 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-22 | 2.26 | 7.4 | 7.6 | 4 | 3 | <5 | <4 | <4 | 1066 | 218 | 5 | 0.4 | 13.9 | 2.18 | <0.005 | <5 | 300.1 | 0.8 | 8400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-08-23 | 2.07 | 7.5 | 7.8 | <2 | <2 | N/S | 4 | <4 | 1134 | 194 | <4 | <0.3 | 16.57 | 2.6 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.006 | 0.07 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 90.5 | 32.23 | 359 | 1 | N/S
2022-08-24 | 2.24 | 7.5 | 7.8 | T/X | T/X | N/S | <4 | <4 | 1180 | 286 | <4 | <0.3 | 18.61 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-25 | 2.28 | 7.5 | 8 | 5 | <2 | N/S | <4 | <4 | 1076 | 156 | <4 | 0.6 | 22.6 | 3.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-26 | 2.24 | 7.5 | 7.2 | N/S | N/S | N/S | 5 | 4 | 1124 | 260 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-27 | 2.44 | 7.4 | 7.6 | N/S | N/S | N/S | 5 | <4 | 1194 | 228 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-28 | 2.3 | 7.5 | 7 | N/S | N/S | N/S | <4 | <4 | 1324 | 226 | <4 | <0.3 | 22.75 | 3.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-29 | 2.77 | 7.5 | 7.6 | <2 | <2 | <5 | <4 | <4 | 1176 | 260 | <4 | <0.3 | 18.05 | 2.97 | <0.005 | <5 | 359.91 | 0.9 | 6400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-08-30 | 3.37 | 7.3 | 7.7 | 2 | <2 | N/S | <4 | <4 | 1094 | 240 | <4 | 0.3 | 12.39 | 2.03 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.008 | 0.04 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | 89.57 | 31.12 | 352 | 1.2 | N/S
2022-08-31 | 2.21 | 7.5 | 8 | 4 | <2 | N/S | 6 | 6 | 1274 | 320 | <4 | 0.4 | 15.83 | 2.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-01 | 2.07 | 7.5 | 7.8 | 4 | <2 | N/S | 6 | 5 | 1398 | 348 | <4 | 0.4 | 19.51 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-02 | 1.97 | 7.5 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1438 | 270 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-03 | 1.97 | 7.4 | 7.3 | N/S | N/S | N/S | 6 | 4 | 1552 | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-04 | 1.85 | 7.3 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1614 | 360 | <4 | 0.3 | 23.12 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-05 | 1.98 | 7.5 | 7.6 | T/X | T/X | <5 | 5 | 4 | 1644 | 366 | <4 | 0.3 | 23.27 | 3.63 | <0.005 | <5 | 543.14 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-06 | 1.91 | 7.4 | 7.6 | T/X | T/X | N/S | 7 | 5 | 1554 | 284 | <4 | 0.4 | 23.98 | 3.53 | N/S | N/S | N/S | N/S | 60000 | <0.002 | 0.05 | <0.002 | <0.004 | 0.005 | 0.05 | 0.04 | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | <3 | 119.76 | 40.52 | 466 | 0.7 | N/S
2022-09-07 | 1.95 | 7.4 | 7.7 | T/X | T/X | N/S | 5 | <4 | 1500 | 236 | <4 | <0.3 | 23.42 | 3.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-08 | 1.95 | 7.4 | 7.6 | T/X | T/X | N/S | <4 | <4 | 1648 | 332 | <4 | 1 | 22.86 | 2.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-09 | 1.88 | 7.4 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1696 | 382 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-10 | 1.92 | 7.5 | 7 | N/S | N/S | N/S | 5 | 4 | 1596 | 354 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-11 | 3.09 | 7.5 | 6.6 | N/S | N/S | N/S | <4 | <4 | 1146 | 242 | <4 | <0.3 | 16.99 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-12 | 3.95 | 7.2 | 7.6 | 5 | 3 | <5 | 7 | 6 | 846 | 170 | 1 | <0.3 | 10.06 | 1.71 | <0.005 | <5 | 239.69 | 0.5 | 68000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-09-13 | 2.34 | 7.3 | 7.5 | 5 | 3 | N/S | 8 | 6 | 966 | 232 | 1 | <0.3 | 11.94 | 1.75 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.008 | 0.07 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 86.85 | 31.59 | 347 | 1.4 | N/S
2022-09-14 | 1.9 | 7.4 | 7.9 | 6 | 3 | N/S | 9 | 8 | 970 | 152 | 2 | 0.8 | 14.17 | 2.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-15 | 2.07 | 7.4 | 7.5 | 10 | 5 | N/S | 17 | 12 | 1198 | 230 | 4 | 2.6 | 16.18 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-16 | 2.94 | 7.3 | 7.4 | N/S | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-17 | 3.63 | 7.4 | 6.9 | N/S | N/S | N/S | 11 | 9 | 1228 | 224 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-18 | 2.21 | 7.5 | 6.5 | N/S | N/S | N/S | 11 | 10 | 1236 | 152 | 16 | 12.1 | 8.24 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-19 | 2.09 | 7.6 | 3.9 | 7 | 3 | <5 | 9 | 7 | 1106 | 156 | 11 | 8.8 | 13.23 | 3.28 | 0.005 | <5 | 301.96 | 0.9 | 41000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-09-20 | 1.86 | 7.5 | 7.8 | 6 | 3 | N/S | 9 | 7 | 1110 | 164 | 8 | 6.3 | 18.18 | 3.66 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.01 | 0.13 | N/S | <0.002 | 0.024 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | 91.98 | 32 | 361 | 1.4 | N/S
2022-09-21 | 1.99 | 7.5 | 7.2 | 9 | 3 | N/S | 9 | 7 | 1198 | 166 | 8 | 6.7 | 18.48 | 3.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-22 | 1.58 | 7.5 | 7.3 | 13 | 5 | N/S | 10 | 9 | 1188 | 174 | 9 | 6.7 | 16.59 | 3.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-23 | 2.07 | 7.6 | 7.6 | N/S | N/S | N/S | 7 | 6 | 1134 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-24 | 1.88 | 7.5 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1226 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-25 | 1.89 | 7.6 | 6.5 | N/S | N/S | N/S | 8 | 7 | 1352 | 250 | 4 | 2.7 | 21.8 | 3.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-26 | 1.83 | 7.5 | 6.7 | 10 | 3 | <5 | 7 | 7 | 1372 | 260 | 3 | 1.2 | 22.65 | 3.7 | 0.005 | <5 | 423.88 | 0.9 | 110000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-09-27 | 1.76 | 7.6 | 6.9 | 8 | 3 | N/S | 8 | 7 | 1332 | 176 | 4 | 0.4 | 23.69 | 3.8 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.009 | 0.11 | N/S | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 96.53 | 31.07 | 369 | 0.9 | N/S
2022-09-28 | 1.74 | 7.5 | 7.8 | 8 | 3 | N/S | 8 | 6 | 1316 | 186 | <4 | 0.3 | 24.78 | 4.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-29 | 1.74 | 7.5 | 6.9 | 7 | 3 | N/S | 5 | 5 | 1280 | 204 | <4 | 0.4 | 25.89 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-30 | 1.75 | 7.4 | 7.4 | N/S | N/S | N/S | 7 | 5 | 1344 | 208 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-01 | 1.78 | 7.4 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1364 | 206 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-02 | 1.8 | 7.4 | 7.3 | N/S | N/S | N/S | 4 | <4 | 1366 | 210 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-03 | 1.74 | 7.4 | 7.3 | 6 | 3 | <5 | 4 | <4 | 1354 | 202 | <4 | 0.3 | 24 | 3.04 | <0.005 | <5 | 432.97 | 1 | 4500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-10-04 | 7.65 | 7.5 | 7.8 | 7 | 2 | N/S | 4 | <4 | 1424 | 234 | <4 | 0.5 | 24.6 | 3.83 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.005 | 0.08 | 0.05 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | 113.46 | 35.24 | 428 | 0.6 | N/S
2022-10-05 | 7.69 | 7.4 | 7.8 | 8 | 3 | N/S | 6 | 5 | 1450 | 272 | <4 | <0.3 | 24.8 | 3.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-06 | 1.69 | 7.6 | 6.5 | 5 | 2 | N/S | <4 | <4 | 1202 | 178 | <4 | 0.3 | 26.73 | 3.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-07 | 1.69 | 7.5 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1306 | 208 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-08 | 1.7 | 7.5 | 7 | N/S | N/S | N/S | <4 | <4 | 1292 | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-09 | 1.68 | 7.5 | 7.6 | N/S | N/S | N/S | 5 | 4 | 1300 | 234 | <4 | <0.3 | 27.37 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-10 | 1.69 | 7.4 | 7.3 | 8 | 3 | <5 | 5 | 5 | 1296 | 226 | <4 | <0.3 | 25.26 | 3.43 | 0.006 | <5 | 350.8 | 1 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-10-11 | 1.89 | 7.4 | 7.4 | 8 | 3 | N/S | 7 | 8 | 1234 | 202 | <4 | <0.3 | 20.97 | 12.84 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.008 | 0.08 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 96.12 | 31.59 | 370 | 0.6 | N/S
2022-10-12 | 2.51 | 7.3 | 8 | 11 | 4 | N/S | 12 | 10 | 974 | 122 | <4 | <0.3 | 18.72 | 2.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-13 | 2.51 | 7.4 | 7.1 | 11 | 4 | N/S | 12 | 9 | 1002 | 130 | <4 | <0.3 | 19.46 | 2.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-14 | 2.13 | 7.4 | 7.9 | N/S | N/S | N/S | 11 | 9 | 1128 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-15 | 1.96 | 7.4 | 7.7 | N/S | N/S | N/S | 8 | 6 | 1084 | 184 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-16 | 1.87 | 7.4 | 7.4 | N/S | N/S | N/S | 6 | 5 | 1160 | 208 | <4 | 0.4 | 24.48 | 3.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-17 | 1.79 | 7.4 | 8 | 6 | <2 | <5 | 8 | 6 | 1140 | 166 | <4 | 0.3 | 23.54 | 3.43 | <0.005 | <5 | 296.4 | 0.9 | 700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-10-18 | 1.78 | 7.4 | 8.1 | 5 | 2 | N/S | 6 | 4 | 1188 | 128 | <4 | <0.3 | 24.76 | 3.31 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 92.57 | 32 | 363 | <0.5 | N/S
2022-10-19 | 1.81 | 7.4 | 8.3 | T/X | T/X | N/S | 4 | 5 | 1232 | 136 | <4 | 0.4 | 23.93 | 3.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-20 | 1.77 | 7.6 | 8.2 | T/X | T/X | N/S | <4 | <4 | 1254 | 192 | <4 | 1.4 | 12.53 | 3.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-21 | 1.72 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1206 | 138 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-22 | 1.79 | 7.6 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1216 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-23 | 1.8 | 7.5 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1286 | 188 | <4 | <0.3 | 26.5 | 3.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-24 | 1.72 | 7.4 | 7.7 | <2 | <2 | <5 | <4 | <4 | 1296 | 202 | <4 | 0.6 | 23.88 | 3.73 | <0.005 | <5 | 389.25 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-10-25 | 2.63 | 7.4 | 8.1 | 3 | <2 | N/S | <4 | <4 | 1028 | 168 | <4 | <0.3 | 19.55 | 3.08 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | 80.29 | 27.59 | 314 | N/S | N/S
2022-10-26 | 3.85 | 7.2 | 8.1 | T/X | T/X | N/S | 7 | 5 | 826 | 92 | <4 | <0.3 | 11.57 | 1.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S
2022-10-27 | 2.19 | 7.4 | 8.3 | T/X | T/X | N/S | 8 | 7 | 958 | 120 | <4 | <0.3 | 15.87 | 2.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-28 | 1.82 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1074 | 110 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-29 | 1.86 | 7.4 | 7.8 | N/S | N/S | N/S | 5 | 5 | 1146 | 120 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-30 | 1.9 | 7.4 | 7.5 | N/S | N/S | N/S | 4 | 4 | 1092 | 138 | <4 | <0.3 | 25.07 | 3.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-31 | 1.86 | 7.4 | 7.8 | 3 | <2 | <5 | 5 | 4 | 1168 | 138 | <4 | <0.3 | 22.39 | 3.7 | <0.005 | <5 | 352.29 | 0.9 | 990 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-11-01 | 1.79 | 7.4 | 7.7 | <2 | <2 | N/S | 5 | <4 | 1156 | 110 | <4 | <0.3 | 25.19 | 3.69 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.007 | 0.05 | 0.04 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | 85.38 | 29.32 | 334 | 0.6 | N/S
2022-11-02 | 7.76 | 7.5 | 8.1 | 5 | <2 | N/S | 6 | 4 | 1156 | 126 | <4 | <0.3 | 27.76 | 3.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-03 | 1.73 | 7.4 | 8.1 | <2 | <2 | N/S | <4 | <4 | 1142 | 118 | <4 | 0.3 | 25.64 | 4.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-04 | 1.95 | 7.5 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1082 | 112 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-05 | 2.41 | 7.4 | 7.4 | N/S | N/S | N/S | <4 | <4 | 960 | 120 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-06 | 2.5 | 7.3 | 7.2 | N/S | N/S | N/S | 6 | 4 | 1030 | 160 | <4 | <0.3 | 18.13 | 2.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-07 | 1.79 | 7.5 | 7.7 | T/X | T/X | <5 | 10 | 8 | 1052 | 142 | 6 | <0.3 | 21.09 | 3.07 | 0.006 | <5 | 321.77 | 0.9 | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-11-08 | 1.7 | 7.4 | 8.4 | T/X | T/X | N/S | 5 | 4 | 992 | 92 | <4 | <0.3 | 24.16 | 3.58 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.006 | 0.05 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 75.59 | 26.78 | 299 | <0.5 | N/S
2022-11-09 | 1.67 | 7.4 | 8.1 | 6 | <2 | N/S | 7 | 5 | 1132 | 160 | <4 | <0.3 | 25.6 | 3.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-10 | 1.68 | 7.4 | 8 | T/X | T/X | N/S | 8 | 7 | 1140 | 134 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-11 | 1.71 | 7.5 | 7.2 | N/S | N/S | N/S | 5 | 4 | 1170 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-12 | 1.73 | 7.4 | 8.6 | N/S | N/S | N/S | 7 | 6 | 1310 | 240 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-13 | 1.73 | 7.4 | 8.3 | N/S | N/S | N/S | 11 | 9 | 1226 | 176 | <4 | <0.3 | 25.28 | 3.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-14 | 1.64 | 7.3 | 8.3 | T/X | T/X | <5 | 13 | 11 | 1184 | 160 | <4 | <0.3 | 24.3 | 3.5 | <0.005 | <5 | 338.34 | 1 | 2100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-11-15 | 1.82 | 7.4 | 8.2 | T/X | T/X | N/S | 12 | 10 | 1180 | 138 | <4 | <0.3 | 25.45 | 3.83 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.008 | 0.09 | N/S | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | 85.87 | 28.56 | 332 | <0.5 | N/S
2022-11-16 | 1.91 | 7.5 | 8.8 | 11 | 5 | N/S | 11 | 9 | 1226 | 144 | <4 | <0.3 | 24.04 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-17 | 1.81 | 7.4 | 8.7 | 15 | 5 | N/S | 10 | 9 | 1212 | 168 | <4 | <0.3 | 25.53 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-18 | 1.72 | 7.6 | 8.9 | N/S | N/S | N/S | 6 | 5 | 1216 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-19 | 1.76 | 7.6 | 9 | N/S | N/S | N/S | 4 | <4 | 1200 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-20 | 1.82 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1264 | 164 | <4 | <0.3 | 24.36 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-21 | 1.76 | 7.5 | 8.8 | T/X | T/X | <5 | <4 | <4 | 1236 | 142 | <4 | <0.3 | 25.13 | 3.51 | <0.005 | <5 | 378.64 | 1 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-11-22 | 1.62 | 7.4 | 8.9 | T/X | T/X | N/S | 7 | 5 | 1294 | 174 | <4 | 0.5 | 21.96 | 3.8 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.007 | 0.08 | N/S | <0.002 | 0.035 | <0.002 | <0.004 | <0.004 | 0.042 | <0.002 | <0.002 | <0.002 | N/S | 81.7 | 27.68 | 318 | <0.5 | N/S
2022-11-23 | 1.84 | 7.4 | 8.4 | T/X | T/X | N/S | 6 | 5 | 1258 | 160 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-24 | 1.78 | 7.5 | 4.9 | T/X | T/X | N/S | 6 | 4 | 1242 | 174 | <4 | <0.3 | 20.27 | 3.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-25 | 1.71 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 4 | 1150 | 110 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-26 | 1.73 | 7.4 | 7.9 | N/S | N/S | N/S | 6 | 4 | 1142 | 104 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-27 | 1.92 | 7.4 | 8.1 | N/S | N/S | N/S | 7 | 6 | 1154 | 112 | <4 | 0.3 | 23.05 | 4.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-28 | 2.01 | 7.3 | 8.3 | T/X | T/X | <5 | 9 | 6 | 1124 | 116 | <4 | <0.3 | 21.38 | 3.9 | 0.005 | <5 | 324.97 | 0.9 | 19000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-11-29 | 1.85 | 7.4 | 8.4 | T/X | T/X | N/S | 7 | 6 | 1166 | 118 | <4 | <0.3 | 21.71 | 3.6 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.006 | 0.06 | N/S | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 83.15 | 29.54 | 329 | <0.5 | N/S
2022-11-30 | 1.91 | 7.4 | 8.9 | T/X | T/X | N/S | 14 | 11 | 1176 | 154 | <4 | <0.3 | 22.93 | 3.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-01 | 1.78 | 7.4 | 9.1 | T/X | T/X | N/S | 5 | 4 | 1136 | 120 | <4 | <0.3 | 23.36 | 3.98 | N/S | N/S | 314.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-02 | 1.71 | 7.5 | 8.3 | N/S | N/S | N/S | 4 | <4 | 1104 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | 297.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-03 | 1.79 | 7.6 | 8 | N/S | N/S | N/S | 6 | 5 | 1172 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | 331.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-04 | 1.82 | 7.5 | 8.3 | N/S | N/S | N/S | 6 | 5 | 1166 | 150 | <4 | 0.7 | 23.13 | 3.75 | N/S | N/S | 340.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-05 | 1.72 | 7.4 | 8.1 | T/X | T/X | <5 | 5 | <4 | 1166 | 134 | <4 | T/X | 21.58 | 4.92 | 0.009 | <5 | 329.08 | 1 | 3100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-12-06 | 1.72 | 7.4 | 8.4 | T/X | T/X | N/S | 5 | 4 | 1126 | 132 | <4 | <0.3 | 21.62 | 3.69 | N/S | N/S | 311.93 | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.007 | 0.06 | 0.04 | <0.002 | 0.02 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 74.75 | 25.54 | 292 | 0.7 | N/S
2022-12-07 | 1.68 | 7.5 | 8.3 | 13 | 6 | N/S | 9 | 8 | 1154 | 136 | <4 | <0.3 | 24.51 | 4.12 | N/S | N/S | 319.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-08 | 1.7 | 7.4 | 8.6 | 11 | 4 | N/S | 16 | 14 | 1204 | 166 | <4 | <0.3 | 23.75 | 4.12 | N/S | N/S | 330.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-09 | 2.02 | 7.4 | 8.7 | N/S | N/S | N/S | 10 | 9 | 1114 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | 306.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-10 | 2.41 | 7.2 | 8.6 | N/S | N/S | N/S | 10 | 8 | 1036 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 289.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-11 | 2.23 | 7.2 | 7.9 | N/S | N/S | N/S | 10 | 8 | 1118 | 202 | <4 | 1 | 18.37 | 2.97 | N/S | N/S | 323.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-12 | 1.77 | 7.3 | 8.1 | 15 | 6 | <5 | 9 | 7 | 1144 | 164 | <4 | 0.3 | 20.33 | 3.14 | <0.005 | <5 | 322.41 | 0.9 | 410000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-12-13 | 1.75 | 7.4 | 8.6 | 8 | 4 | N/S | 6 | 5 | 1030 | 128 | <4 | <0.3 | 23.05 | 3.34 | N/S | N/S | 273.04 | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.008 | 0.07 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 71.88 | 25.31 | 284 | 1.1 | N/S
2022-12-14 | 2.75 | 7.3 | 8.7 | 13 | 6 | N/S | 12 | 11 | 766 | 114 | <4 | <0.3 | 17.33 | 2.92 | N/S | N/S | 184.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-15 | 4.1 | 7 | 8 | 9 | 5 | N/S | 7 | 6 | 588 | 110 | 1 | <0.3 | 9.56 | 1.41 | N/S | N/S | 155.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-16 | 4.08 | 7.6 | 10.1 | N/S | N/S | N/S | 8 | 7 | 798 | 112 | N/S | N/S | N/S | N/S | N/S | N/S | 212.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-17 | 3.59 | 7.2 | 7.8 | N/S | N/S | N/S | <4 | <4 | 900 | 96 | N/S | N/S | N/S | N/S | N/S | N/S | 259.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-18 | 2.25 | 7.4 | 8.1 | N/S | N/S | N/S | 7 | 6 | 990 | 112 | <4 | 0.4 | 16.75 | 2.01 | N/S | N/S | 279.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-19 | 2.31 | 7.3 | 8.9 | T/X | T/X | <5 | 8 | 7 | 1042 | 108 | <4 | <0.3 | 19.5 | 2.52 | <0.005 | <5 | 291.13 | 0.8 | 6300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2022-12-20 | 2.13 | 7.5 | 8.7 | T/X | T/X | N/S | 8 | 7 | 1046 | 142 | <4 | <0.3 | 20 | 2.7 | N/S | N/S | 266.48 | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.009 | 0.08 | N/S | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 71.64 | 26.98 | 290 | 1.7 | N/S
2022-12-21 | 2.04 | 7.4 | 8.9 | T/X | T/X | N/S | 12 | 9 | 1000 | 110 | <4 | 0.7 | 17.84 | 2.84 | N/S | N/S | 262.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-22 | 1.89 | 7.4 | 8.2 | T/X | T/X | N/S | 7 | 6 | 1086 | 142 | <4 | 0.5 | 15.96 | 2.77 | N/S | N/S | 289.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-23 | 1.98 | 7.4 | 9 | N/S | N/S | N/S | 8 | 7 | 830 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | 301.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-24 | 2.06 | 7.4 | 8.8 | N/S | N/S | N/S | 10 | 9 | 1086 | 120 | N/S | N/S | N/S | N/S | N/S | N/S | 286.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-25 | 2.01 | 7.3 | 8.9 | N/S | N/S | N/S | 23 | 20 | 1148 | 138 | T/X | T/X | T/X | T/X | N/S | N/S | 323.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-26 | 1.91 | 7.4 | 8.3 | 20 | 5 | <5 | 12 | 10 | 1062 | 122 | 6 | 3.6 | 8.02 | 3.44 | 0.008 | <5 | 304.33 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-27 | 1.9 | 7.5 | 8.3 | 15 | 4 | N/S | 8 | 6 | 1144 | 126 | 4 | 2.2 | 7.94 | 3.52 | N/S | N/S | 339.62 | N/S | 12000 | <0.002 | 0.037 | <0.002 | <0.004 | 0.008 | 0.09 | N/S | <0.002 | 0.046 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | <3 | 80.43 | 28.22 | 317 | 0.8 | N/S
2022-12-28 | 1.94 | 7.4 | 8.2 | 17 | 5 | N/S | 12 | 10 | 1256 | 122 | 3 | 1.1 | 8.57 | 3.14 | N/S | N/S | 411.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-29 | 2.3 | 7.4 | 8 | 11 | 4 | N/S | 6 | 6 | 1332 | 136 | 3 | 1.2 | 7.46 | 2.9 | N/S | N/S | 470.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-30 | 2.36 | 7.3 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1292 | 168 | N/S | N/S | N/S | N/S | N/S | N/S | 439.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-31 | 2.37 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 1210 | 146 | N/S | N/S | N/S | N/S | N/S | N/S | 411.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
RL effective 1/1/22 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 50 | 1 | 0.3 | 0.25 | 0.15 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.002 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
RL effective 10/1/22 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 50 | 1 | 0.3 | 0.5 | 0.15 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.002 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
Observations | 365 | 365 | 365 | 121 | 121 | 51 | 361 | 361 | 361 | 361 | 247 | 245 | 246 | 247 | 52 | 52 | 182 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 11 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 51 | 51 | 51 | 52 | 0
Minimum | 1.43 | 6.9 | 3.7 | <2 | <2 | <5 | <4 | <4 | 520 | 82 | <1 | <0.3 | 7.17 | 0.85 | <0.005 | <5 | 155.1 | 0.5 | 500 | <0.002 | 0.031 | <0.002 | <0.004 | 0.005 | 0.04 | 0.04 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | <3 | 71.64 | 25.31 | 284 | <0.5
Mean | 2.63 | 7.4 | 7.7 | <9 | <4 | <4 | <7 | <6 | 1228 | 182 | <3 | <0.7 | 17.31 | 2.78 | <0.004 | <4 | 411.48 | 0.8 | GM=8991 | <0.001 | 0.042 | <0.001 | <0.003 | 0.008 | 0.09 | 0.05 | <0.001 | 0.018 | <0.001 | <0.003 | <0.003 | 0.029 | <0.001 | <0.001 | <0.001 | <2 | 94.27 | 32.7 | 370 | <1.2
Maximum | 7.76 | 8.1 | 10.1 | 24 | 16 | <5 | 29 | 24 | 2100 | 470 | 16 | 12.1 | 27.76 | 12.84 | 0.009 | 8 | 990.25 | 1 | 450000 | <0.002 | 0.052 | <0.002 | <0.004 | 0.014 | 0.15 | 0.09 | <0.002 | 0.114 | <0.002 | <0.004 | <0.004 | 0.042 | <0.002 | <0.002 | <0.002 | <3 | 124.62 | 40.52 | 475 | 10.7
%>400=100
*Effective 1/1/21, means are no longer calculated using the Reporting Limit value in place of non-detect/<LOQ results and are now calculated by replacing any non-detect/<LOQ results with the Reporting Limit/(SQRT2).
January 3, 4, 5, 6, 10, 11, 2022, BOD5, CBOD, T/X: Method required temperature lost due to incubator failure.
January 16, 2022, TKN, NH3, NO2+NO3, TOT-P, T/X: Sample was not preserved within holding time.
January 17, 18, 31, 2022, BOD5, CBOD, T/X: LCS failure.
January 24, 2022, TKN: Sample MS recovery failed but LCS passed.
February 1, 7, 8, 9, 2022, BOD5, CBOD, T/X: LCS failure.
February 10, 2022, BOD5, CBOD, TKN, NH3, NO2+NO3, TOT-P, T/X: Sample not composited due to holiday.
February 17, 2022, TKN, P-TOT: Sample MS recovery failed but LCS passed.
February 20, 2022, TKN, NH3, NO2+NO3, TOT-P, T/X: Sample was not preserved within holding time.
March 1, 21, 2022, FOG, T/X: LCS failure.
March 14, 15, 17, 2022, BOD5, CBOD, T/X: Method required temperature lost due to incubator failure.
March 16, 2022, BOD5, CBOD, T/X: Sample collection error.
March 21, 22, 23, 24, 2022, BOD5, CBOD, T/X: LCS failure.
March 28, 2022, NH3, NO2+NO3: Sample MS recovery failed but LCS passed.
March 30, 2022, Cl: Sample MS recovery failed but LCS passed.
April 5, 2022, Cl: Sample MS/MSD recovery failed but LCS passed.
April 13, 21, 2022, NH3-N, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
May 2, 11-12, 18-19, 25-26, 2022, BOD5, CBOD5, T/X: Incubator failure.
May 3-5, 2022, Various Tests, S/X: Sampling point out of service.
May 29, 2022, TKN, NH3, NO2+NO3, TOT-P, T/X: Sample was not preserved within holding time.
May 30-31, 2022, BOD5, CBOD5, T/X: LCS failure.
June 5, 6, 2022, TKN, TOT-P: Sample MS/MSD recovery failed but LCS passed.
June 13-16, 2022, BOD5, CBOD5, T/X: Incubator failure.
June 14, 23, 2022, NH3-N, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
June 19,2022, TKN, NH3, NO2+NO3, TOT-P, T/X: Sample was not preserved within holding time.
June 29, 2022, BOD5, CBOD5, T/X: Method blank failure.
June 30, 2022 BOD5, CBOD5, T/X: LCS failure.
July 3, 2022, TKN, NH3, NO2+NO3, P-TOT, T/X: Aliquots were not preserved within holding time.
July 4, 5, 2022, BOD5, CBOD5: Dilution water blank failure.
July 4, 2022, NH3: Sample MS/MSD recovery failed but LCS passed.
July 4, 6, 2022, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
July 6, 2022, BOD5, CBOD5, T/X: None of the dilutions met acceptance criteria.
July 10, 2022, NH3, NO2+NO3, T/X: Sample was mixed up with another sample during analysis.
July 11-14, 20,21, 2022, BOD5, CBOD5, T/X: Incubator failure.
July 25, 26, 2022, BOD5, CBOD5, T/X: LCS failure.
August 1, 2022, FOG: Sample MS/MSD recovery failed but LCS passed.
August 8-11, 17, 18, 2022, BOD5, CBOD5, T/X: Incubator failure.
August 9, 18, 2022, TKN, P-TOT: Sample MS/MSD recovery failed but LCS passed.
August 15, 16, 24, 2022, BOD5, CBOD5, T/X: Dilution water blank failure.
August 21, 2022, NH3, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
August 30, 2022, Ag: Sample MS recovery failed but LCS passed.
September 5-8, 2022, BOD5, CBOD5, T/X: LCS failure.
September 14, 2022, NH3, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
September 16, 2022, ALL TESTS, S/X: Sample point out of service.
October 2, 2022, TKN, NH3, NO2+NO3, P-TOT, T/X: Sample not aliquoted or preserved.
October 6, 2022, P-TOT: Sample MS recovery failed but LCS passed.
October 12, 17, 2022, NO2+NO3: Sample MS recovery failed but LCS passed.
October 17, 2022, Cr6+: Sample MS recovery failed but LCS passed.
October 19, 20, 26, 27, 2022, BOD5, CBOD5, T/X: Incubator failure.
October 30, 2022, NH3: Sample MS recovery failed but LCS passed.
November 3, 13, 28, 2022, TKN: Sample MS recovery failed but LCS passed.
November 7, 8, 14, 15, 28, 29, 30, 2022, BOD5, CBOD5, T/X: LCS failure.
November 10, 23, 2022, BOD5, CBOD5, T/X: Canceled due to holiday.
November 10, 23, 2022, TKN, NH3, NO2+NO3, P-TOT, T/X: Sample not aliquoted or preserved.
November 15, 2022, P-TOT: Sample MS recovery failed but LCS passed.
November 17, 2022, NH3, NO2+NO3: Sample MS recovery failed but LCS passed.
November 21, 22, 2022, BOD5, CBOD5, T/X: LCS and blank failure.
November 24, 2022, BOD5, CBOD5, T/X: Blank failure.
November 30, 2022, NO2+NO3: Sample MS recovery failed but LCS passed.
December 1, 5, 6, 2022, BOD5, CBOD5, T/X: LCS failure.
December 5, 2022, NH3, T/X: Precision failure.
December 6, 7, 28, 2022, NO2+NO3: Sample MS recovery failed but LCS passed.
December 12, 2022, FOG: Sample MS recovery failed but LCS passed.
December 18, 2022, TKN: Sample MS recovery failed but LCS passed.
December 19-22, 2022, BOD5, CBOD5, T/X: Incubator failure.
December 25, 2022, TKN, NH3, NO2+NO3, P-TOT, T/X: Sample not aliquoted or preserved.

## Lemont Outfall 2023
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2023-01-01 | 2.35 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1180 | 160 | T/X | T/X | T/X | T/X | N/S | N/S | 397.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-02 | 2.26 | 7.3 | 8.5 | 10 | 4 | <5 | 5 | <4 | 1284 | 148 | <4 | 0.5 | 14.07 | 2.84 | <0.005 | <5 | 425.45 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-03 | 3.45 | 7.3 | 8.7 | 10 | 5 | N/S | 10 | 8 | 968 | 128 | <4 | 0.7 | 11.07 | 1.94 | N/S | N/S | 339.91 | N/S | 22000 | <0.002 | 0.035 | <0.002 | <0.004 | 0.007 | 0.08 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | <3 | 75.18 | 27.02 | 299 | 0.6 | N/S
2023-01-04 | 3.82 | 7.2 | 8.6 | 7 | 4 | N/S | 6 | 5 | 992 | 140 | 1 | <0.5 | 10.4 | 1.38 | N/S | N/S | 315.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-05 | 3.78 | 7.3 | 8.8 | 8 | 4 | N/S | 6 | 5 | 1032 | 154 | <4 | <0.5 | 11.49 | 1.6 | N/S | N/S | 334.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-06 | 3.1 | 7.2 | 8.4 | N/S | N/S | N/S | 4 | <4 | 1186 | 280 | N/S | N/S | N/S | N/S | N/S | N/S | 377.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-07 | 2.35 | 7.4 | 9.2 | N/S | N/S | N/S | 4 | <4 | 1218 | 254 | N/S | N/S | N/S | N/S | N/S | N/S | 383.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-08 | 2.32 | 7.3 | 9 | N/S | N/S | N/S | 4 | 4 | 1250 | 226 | <4 | <0.5 | 19.06 | 2.72 | N/S | N/S | 386.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-09 | 2.18 | 7.3 | 8.9 | 7 | 3 | <5 | 4 | <4 | 1228 | 188 | <4 | <0.5 | 18.16 | 2.74 | <0.005 | <5 | 377.74 | 0.8 | 4100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-01-10 | 2.13 | 7.4 | 8.7 | 3 | <2 | N/S | <4 | <4 | 1170 | 164 | <4 | <0.5 | 17.47 | 2.75 | N/S | N/S | 349.79 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.005 | 0.04 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | 89.33 | 32.75 | 358 | 1.1 | N/S
2023-01-11 | 2.01 | 7.4 | 8.8 | 6 | 2 | N/S | 5 | 4 | 1148 | 130 | <4 | <0.5 | 20.14 | 2.89 | N/S | N/S | 344.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-12 | 1.99 | 7.5 | 8.1 | 7 | 3 | N/S | 4 | 5 | 1158 | 124 | <4 | <0.5 | 19.23 | 3.36 | N/S | N/S | 353.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-13 | 1.87 | 7.5 | 8.8 | N/S | N/S | N/S | <4 | <4 | 1156 | 126 | N/S | N/S | N/S | N/S | N/S | N/S | 329.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-14 | 1.9 | 7.5 | 9.2 | N/S | N/S | N/S | <4 | <4 | 1226 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | 337.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-15 | 1.93 | 7.5 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1172 | 126 | T/X | T/X | T/X | T/X | N/S | N/S | 331.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-16 | 1.99 | 7.5 | 8.3 | 5 | <2 | <5 | <4 | <4 | 1160 | 140 | <4 | 0.7 | 15 | 2.87 | <0.005 | <5 | 334.1 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-17 | 2.23 | 7.3 | 8.5 | 8 | 4 | N/S | 7 | 6 | 1200 | 134 | 1 | <0.5 | 12.66 | 2.45 | N/S | N/S | 369.61 | N/S | 1500 | <0.002 | 0.04 | <0.002 | <0.004 | 0.005 | 0.07 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | <3 | 85.88 | 31.8 | 345 | 0.6 | N/S
2023-01-18 | 2.56 | 7.4 | 8.8 | 12 | 7 | N/S | 18 | 15 | 1162 | 136 | 2 | <0.5 | 13.95 | 2.67 | N/S | N/S | 364.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-19 | 3.86 | 7.2 | 7.6 | 15 | 7 | N/S | 34 | 29 | 1026 | 104 | 3 | <0.5 | 10.17 | 2.02 | N/S | N/S | 351.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-20 | 2.93 | 7.2 | 8.7 | N/S | N/S | N/S | 11 | 9 | 996 | 110 | N/S | N/S | N/S | N/S | N/S | N/S | 325.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-21 | 2.24 | 7.4 | 8.8 | N/S | N/S | N/S | 9 | 8 | 1044 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | 310.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-22 | 2.17 | 7.3 | 8.2 | N/S | N/S | N/S | 8 | 7 | 1150 | 172 | <4 | <0.5 | 17.82 | 2.63 | N/S | N/S | 351.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-23 | 2.48 | 7.3 | 8.3 | S/X | S/X | <5 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | <0.005 | N/S | S/X | S/X | 4200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-01-24 | 2.12 | 7.4 | 9.1 | 11 | 4 | N/S | 10 | 8 | 1150 | 186 | <4 | <0.5 | 17.93 | 2.69 | N/S | <5 | 358.96 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.008 | 0.09 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | 89.15 | 36.95 | 375 | 1.3 | N/S
2023-01-25 | 2.81 | 7.4 | 8.8 | 11 | 5 | N/S | 7 | 6 | 1482 | 198 | <4 | 0.6 | 16.63 | 2.82 | N/S | N/S | 558.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-26 | 2.53 | 7.2 | 7.8 | 11 | 5 | N/S | 10 | 8 | 1750 | 150 | <4 | <0.5 | 14.73 | 2.32 | N/S | N/S | 718.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-27 | 2.49 | 7.3 | 9.4 | N/S | N/S | N/S | 4 | 4 | 1682 | 184 | N/S | N/S | N/S | N/S | N/S | N/S | 658.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-28 | 2.38 | 7.3 | 9.4 | N/S | N/S | N/S | 5 | 4 | 1578 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 603.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-29 | 2.08 | 7.4 | 8.9 | N/S | N/S | N/S | 4 | <4 | 1602 | 144 | <4 | <0.5 | 24.72 | 2.56 | N/S | N/S | 574.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-30 | 2.34 | 7.3 | 9.3 | 11 | 5 | <5 | 7 | 6 | 1636 | 140 | 5 | 1 | 19.75 | 2.96 | <0.005 | <5 | 585.49 | 0.8 | 29000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-01-31 | 2.14 | 7.4 | 9.1 | 15 | 8 | N/S | 15 | 12 | 1592 | 148 | 3 | <0.5 | 19.85 | 2.94 | N/S | N/S | 538.11 | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.009 | 0.11 | N/S | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | 101.19 | 37.01 | 405 | 1.2 | N/S
2023-02-01 | 1.96 | 7.4 | 9.2 | 15 | 8 | N/S | 14 | 12 | 1326 | 136 | <4 | <0.5 | 22.31 | 2.92 | N/S | N/S | 443.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-02 | 1.99 | 7.3 | 9 | 18 | 8 | N/S | 15 | 13 | 1254 | 144 | <4 | <0.5 | 22.88 | 3 | N/S | N/S | 405.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-03 | 1.92 | 7.4 | 9.1 | N/S | N/S | N/S | 22 | 18 | 1392 | 204 | N/S | N/S | N/S | N/S | N/S | N/S | 426.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-04 | 1.95 | 7.3 | 9.1 | N/S | N/S | N/S | 21 | 18 | 1534 | 356 | N/S | N/S | N/S | N/S | N/S | N/S | 429.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-05 | 2.07 | 7.3 | 7.8 | N/S | N/S | N/S | 19 | 16 | 1356 | 188 | <4 | <0.5 | 20.48 | 3.05 | N/S | N/S | 435.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-06 | 2.09 | 7.3 | 8.3 | 21 | 9 | <5 | 16 | 14 | 1412 | 202 | <4 | <0.5 | 18.66 | 2.83 | <0.005 | <5 | 445.74 | 0.9 | 120000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-02-07 | 2.02 | 7.3 | 8.6 | 19 | 8 | N/S | 16 | 13 | 1350 | 184 | <4 | <0.5 | 20.58 | 2.88 | N/S | N/S | 446.67 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.013 | 0.12 | 0.05 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.041 | <0.002 | <0.002 | <0.002 | N/S | 91.66 | 32.94 | 365 | 1.4 | N/S
2023-02-08 | 2.1 | 7.3 | 8.6 | T/X | T/X | N/S | 17 | 13 | 1300 | 178 | <4 | 0.7 | 20.55 | 2.77 | N/S | N/S | 432.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-09 | 3.49 | 7 | 8.4 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-10 | 4.04 | 7.2 | 9.1 | N/S | N/S | N/S | 8 | 7 | 1188 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | 427.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-11 | 3.8 | 7.3 | 8.8 | N/S | N/S | N/S | 7 | 7 | 1198 | 182 | N/S | N/S | N/S | N/S | N/S | N/S | 420.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-12 | 3.95 | 7.3 | 7.7 | N/S | N/S | N/S | 6 | 5 | 1140 | 144 | T/X | T/X | T/X | T/X | N/S | N/S | 388.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-13 | 3.03 | 7.3 | 7.1 | 24 | 9 | <5 | 16 | 14 | 1182 | 146 | 4 | 1.7 | 13.22 | 2.29 | <0.005 | <5 | 389.98 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-14 | 2.82 | 7.3 | 8.5 | 18 | 8 | N/S | 15 | 13 | 1150 | 160 | 3 | 1.4 | 15.2 | 2.29 | N/S | N/S | 368.54 | N/S | 3300 | <0.002 | 0.044 | <0.002 | <0.004 | 0.013 | 0.12 | N/S | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.042 | <0.002 | <0.002 | <0.002 | <3 | 91.01 | 34.31 | 369 | 1.8 | N/S
2023-02-15 | 3.14 | 7.2 | 7.5 | 5 | 5 | N/S | 10 | 8 | 1014 | 108 | 2 | 0.7 | 11.34 | 1.84 | N/S | N/S | 365.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-16 | 3.41 | 7.4 | 9.4 | 11 | 6 | N/S | 9 | 8 | 1114 | 170 | <4 | <0.5 | 15.21 | 1.79 | N/S | N/S | 385.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-17 | 4.01 | 7.2 | 8.4 | N/S | N/S | N/S | 7 | 6 | 1246 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | 445.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-18 | 3.56 | 7.2 | 8.6 | N/S | N/S | N/S | 7 | 6 | 1272 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | 436.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-19 | 2.74 | 7.3 | 8.9 | N/S | N/S | N/S | 7 | 6 | 1230 | 188 | T/X | T/X | T/X | T/X | N/S | N/S | 408.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-20 | 2.3 | 7.3 | 7.6 | T/X | T/X | <5 | 8 | 7 | 1282 | 198 | <4 | <0.5 | 16.31 | 2.34 | <0.005 | <5 | 429.15 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-21 | 2.92 | 7.4 | 8.9 | T/X | T/X | N/S | 11 | 10 | 1252 | 192 | 3 | 1.4 | 15.2 | 2.57 | N/S | N/S | 405.37 | N/S | 8200 | <0.002 | 0.046 | <0.002 | <0.004 | 0.011 | 0.12 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.038 | <0.002 | <0.002 | <0.002 | <3 | 89.46 | 35.73 | 370 | 1.3 | N/S
2023-02-22 | 3.2 | 7.3 | 8.2 | 10 | 8 | N/S | 10 | 9 | 1294 | 206 | <4 | <0.5 | 14.76 | 2.13 | N/S | N/S | 407.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-23 | 4.1 | 7.2 | 9.4 | 7 | 4 | N/S | <4 | <4 | 964 | 162 | <1 | <0.5 | 9.43 | 1.13 | N/S | N/S | 357.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-24 | 4.1 | 7.3 | 10.1 | N/S | N/S | N/S | <4 | <4 | 1070 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | 371.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-25 | 3.99 | 7.3 | 8.8 | N/S | N/S | N/S | <4 | <4 | 1070 | 184 | N/S | N/S | N/S | N/S | N/S | N/S | 359.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-26 | 3.76 | 7.3 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1102 | 172 | <4 | 1.2 | 12.33 | 1.68 | N/S | N/S | 356.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-27 | 7.78 | 7.3 | 8.5 | 6 | 4 | <5 | 7 | 6 | 860 | 134 | 1 | <0.5 | 8.67 | 1.28 | <0.005 | <5 | 297.02 | 0.5 | 4600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-02-28 | 4.1 | 7.4 | 10 | 5 | 3 | N/S | 5 | 4 | 856 | 140 | <1 | <0.5 | 8.79 | 0.94 | N/S | N/S | 290.91 | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.005 | 0.07 | N/S | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | 66.51 | 27.56 | 280 | 1.6 | N/S
2023-03-01 | 4.1 | 7.3 | 9.2 | 4 | <2 | N/S | 5 | 4 | 910 | 134 | 2 | <0.5 | 11.01 | 1.14 | N/S | N/S | 305.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-02 | 4.1 | 7.2 | 8.3 | 5 | 3 | N/S | 6 | 5 | 928 | 122 | <4 | <0.5 | 12.95 | 1.32 | N/S | N/S | 300.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-03 | 3.88 | 7.2 | 8.5 | N/S | N/S | N/S | 7 | 6 | 1032 | 178 | N/S | N/S | N/S | N/S | N/S | N/S | 315 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-04 | 2.53 | 7.2 | 8.3 | N/S | N/S | N/S | 6 | 5 | 1052 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | 312.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-05 | 2.37 | 7.3 | 9.2 | N/S | N/S | N/S | 6 | 4 | 1068 | 154 | <4 | <0.5 | 19.33 | 2.18 | N/S | N/S | 307.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-06 | 3.33 | 7.3 | 8.8 | 11 | 6 | <5 | 8 | 6 | 1132 | 226 | <4 | 0.9 | 16.97 | 2.16 | <0.005 | <5 | 317.77 | 0.7 | 1300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-03-07 | 2.36 | 7.3 | 8.8 | 8 | 5 | N/S | 6 | 4 | 1066 | 174 | <4 | <0.5 | 16.5 | 2.42 | N/S | N/S | 309.88 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.007 | 0.08 | 0.05 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | 81.98 | 33.45 | 342 | 1.3 | N/S
2023-03-08 | 2.36 | 7.5 | 9.2 | 7 | 4 | N/S | 6 | 6 | 1054 | 154 | <4 | <0.5 | 17.57 | 2.63 | N/S | N/S | 306.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-09 | 2.37 | 7.4 | 9.4 | 8 | 5 | N/S | 6 | 5 | 1090 | 132 | <4 | <0.5 | 22.11 | 2.68 | N/S | N/S | 292.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-10 | 3.15 | 7.4 | 9.3 | N/S | N/S | N/S | <4 | <4 | 1124 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | 311.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-11 | 2.61 | 7.3 | 8 | N/S | N/S | N/S | <4 | <4 | 1072 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | 315.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-12 | 2.85 | 7.4 | 8.7 | N/S | N/S | N/S | 4 | <4 | 1194 | 218 | <4 | <0.5 | 15.91 | 2.14 | N/S | N/S | 385.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-13 | 3.56 | 7.2 | 8.1 | 4 | 3 | 5 | 5 | 4 | 1162 | 154 | <4 | <0.5 | 13.32 | 1.72 | 0.006 | <5 | 369.5 | 0.6 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-03-14 | 2.26 | 7.4 | 8.5 | 7 | 4 | N/S | 6 | 5 | 1134 | 156 | <4 | <0.5 | 14.64 | 1.86 | N/S | N/S | 358.72 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | 83.61 | 34.51 | 351 | 0.8 | N/S
2023-03-15 | 2.74 | 7.4 | 9.4 | 8 | 4 | N/S | 6 | 6 | 1228 | 262 | <4 | <0.5 | 16.98 | 2.16 | N/S | N/S | 344.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-16 | 2.37 | 7.3 | 8.8 | 7 | 4 | N/S | 6 | 5 | 1126 | 178 | <4 | <0.5 | 17.55 | 2.5 | N/S | N/S | 331.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-17 | 3.15 | 7.3 | 9.1 | N/S | N/S | N/S | 6 | 4 | 1062 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | 360.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-18 | 2.53 | 7.3 | 10 | N/S | N/S | N/S | 6 | 5 | 1050 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | 334.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-19 | 2.57 | 7.4 | 9.8 | N/S | N/S | N/S | 6 | 5 | 1092 | 142 | <4 | <0.5 | 14.8 | 2.19 | N/S | N/S | 358.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-20 | 2.58 | 7.2 | 9.1 | 9 | 4 | <5 | 6 | 6 | 1212 | 208 | <4 | <0.5 | 19.49 | 2.39 | <0.005 | <5 | 358.97 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-03-21 | 2.5 | 7.4 | 9.2 | 8 | 4 | N/S | 6 | 5 | 1212 | 178 | <4 | <0.5 | 16.03 | 2.33 | N/S | N/S | 354.19 | N/S | 73000 | <0.002 | 0.043 | <0.002 | <0.004 | 0.006 | 0.06 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | 91.21 | 36.15 | 377 | 0.6 | N/S
2023-03-22 | 3.58 | 7.3 | 9.1 | 10 | 4 | N/S | <4 | <4 | 1116 | 106 | 3 | 2.2 | 13.9 | 2.4 | N/S | N/S | 366.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-23 | 3.38 | 7.3 | 8.2 | 5 | 4 | N/S | <4 | <4 | 1070 | 152 | <4 | 0.6 | 12.89 | 1.96 | N/S | N/S | 367.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-24 | 2.59 | 7.4 | 9.3 | N/S | N/S | N/S | 8 | 7 | 1016 | 126 | N/S | N/S | N/S | N/S | N/S | N/S | 336.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-25 | 3.78 | 7.3 | 9.6 | N/S | N/S | N/S | <4 | <4 | 820 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | 275.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-26 | 4.1 | 7.4 | 9.4 | N/S | N/S | N/S | <4 | <4 | 846 | 94 | <4 | <0.5 | 10.09 | 1.17 | N/S | N/S | 279.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-27 | 4.1 | 7.2 | 8.9 | 4 | <2 | <5 | <4 | <4 | 724 | 92 | <1 | <0.5 | 9.84 | 1.17 | <0.005 | <5 | 280.3 | 0.5 | 6600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-03-28 | 4.1 | 7.3 | 9.4 | 4 | <2 | N/S | 4 | 4 | 922 | 114 | <4 | <0.5 | 11.97 | 1.31 | N/S | N/S | 284.56 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | 75.58 | 31.47 | 318 | 2 | N/S
2023-03-29 | 4.08 | 7.2 | 9 | 5 | 3 | N/S | 5 | 5 | 1004 | 160 | <4 | <0.5 | 13.1 | 2.97 | N/S | N/S | 296.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-30 | 3.82 | 7.3 | 8.4 | 7 | 4 | N/S | 7 | 6 | 942 | 94 | 1 | <0.5 | 13.93 | 1.73 | N/S | N/S | 287.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-31 | 2.94 | 7.3 | 8.5 | N/S | N/S | N/S | 5 | 4 | 1038 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | 295.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-01 | 3.86 | 7.2 | 7.9 | N/S | N/S | N/S | 5 | 6 | 1140 | 242 | N/S | N/S | N/S | N/S | N/S | N/S | 303.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-02 | 2.84 | 7.2 | 8.8 | N/S | N/S | N/S | 4 | 4 | 1076 | 206 | 5 | <0.3 | 12.96 | 1.78 | N/S | N/S | 292.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-03 | 3.33 | 7.4 | 9.3 | 8 | 4 | <5 | 8 | 6 | 916 | 84 | <4 | <0.3 | 14.55 | 2.01 | <0.005 | <5 | 282.61 | 0.7 | 3300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-04-04 | 3.18 | 7.3 | 8.5 | 8 | 5 | N/S | 6 | 6 | 884 | 84 | <4 | <0.3 | 13.48 | 1.97 | N/S | N/S | 283.93 | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.008 | 0.08 | 0.05 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | 85.23 | 35.72 | 360 | 1.6 | N/S
2023-04-05 | 3.46 | 7.3 | 8.6 | T/X | T/X | N/S | 6 | 6 | 924 | 132 | <4 | <0.3 | 12.68 | 1.69 | N/S | N/S | 275.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-06 | 3.68 | 7.3 | 9 | T/X | T/X | N/S | 6 | 6 | 898 | 94 | <4 | <0.3 | 12.41 | 1.7 | N/S | N/S | 264.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-07 | 2.5 | 7.4 | 9.5 | N/S | N/S | N/S | <4 | <4 | 910 | 94 | N/S | N/S | N/S | N/S | N/S | N/S | 265.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-08 | 2.81 | 7.4 | 7.5 | N/S | N/S | N/S | 9 | 7 | 1010 | 140 | N/S | N/S | N/S | N/S | N/S | N/S | 283.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-09 | 2.91 | 7.4 | 8.4 | N/S | N/S | N/S | 10 | 8 | 1052 | 130 | 4 | 2.5 | 13.02 | 2.55 | N/S | N/S | 297.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-10 | 2.26 | 7.4 | 7.4 | 17 | 8 | <5 | 10 | 9 | 1050 | 132 | 4 | 2.1 | 12.99 | 2.9 | <0.005 | <5 | 309.98 | 0.8 | 55000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-04-11 | 2.19 | 7.4 | 8.3 | 12 | 7 | N/S | 9 | 7 | 1070 | 142 | <4 | <0.3 | 15.82 | 2.62 | N/S | N/S | 305.84 | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.011 | 0.1 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 106.54 | 42.97 | 443 | 0.6 | N/S
2023-04-12 | 2.63 | 7.4 | 8.2 | 14 | 6 | N/S | 11 | 9 | 1074 | 150 | 2 | 1.3 | 14.75 | 2.81 | N/S | N/S | 305.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-13 | 2.13 | 7.3 | 7.8 | 8 | 6 | N/S | 8 | 8 | 1060 | 144 | <4 | 0.4 | 16.17 | 2.77 | N/S | N/S | 290.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-14 | 2.14 | 7.3 | 8.1 | N/S | N/S | N/S | 9 | 8 | 1124 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | 307.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-15 | 2.16 | 7.3 | 7.7 | N/S | N/S | N/S | 7 | 7 | 1218 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | 353.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-16 | 2.18 | 7.3 | 7.6 | N/S | N/S | N/S | 11 | 9 | 1218 | 186 | 2 | <0.3 | 16.99 | 3.18 | N/S | N/S | 359.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-17 | 2.22 | 7.3 | 8.2 | T/X | T/X | <5 | 13 | 11 | 1190 | 196 | <4 | <0.3 | 17.43 | 2.75 | <0.005 | <5 | 343.81 | 0.8 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-04-18 | 2.51 | 7.4 | 8.7 | T/X | T/X | N/S | 11 | 10 | 1236 | 202 | <4 | 0.8 | 17.76 | 2.67 | N/S | N/S | 370.48 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.013 | 0.11 | N/S | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 98.71 | 38.26 | 404 | <0.5 | N/S
2023-04-19 | 2.16 | 7.4 | 8.6 | T/X | T/X | N/S | 10 | 10 | 1278 | 270 | <4 | <0.3 | 18.87 | 2.8 | N/S | N/S | 353.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-20 | 2.58 | 7.4 | 8.4 | T/X | T/X | N/S | 9 | 8 | 1142 | 214 | <4 | <0.3 | 17.4 | 2.63 | N/S | N/S | 322.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-21 | 2.53 | 7.4 | 8.6 | N/S | N/S | N/S | 4 | <4 | 1126 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | 341.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-22 | 2.15 | 7.4 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1232 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | 387.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-23 | 2.14 | 7.4 | 7 | N/S | N/S | N/S | 5 | 4 | 1284 | 236 | <4 | <0.3 | 19.32 | 3.11 | N/S | N/S | 367.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-24 | 2.12 | 7.5 | 9 | 8 | 4 | <5 | 4 | <4 | 1196 | 174 | <4 | <0.3 | 19.26 | 3.17 | <0.005 | <5 | 322.21 | 0.9 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-04-25 | 2.04 | 7.4 | 8.6 | 11 | 6 | N/S | 10 | 8 | 1178 | 182 | <4 | <0.3 | 18.99 | 3.17 | N/S | N/S | 331.98 | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.012 | 0.1 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | 93.27 | 37.07 | 386 | 0.9 | N/S
2023-04-26 | 2.09 | 7.4 | 8.5 | T/X | T/X | N/S | 10 | 8 | 1168 | 168 | <4 | <0.3 | 19.34 | 3.32 | N/S | N/S | 332.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-27 | 2.05 | 7.3 | 8.1 | T/X | T/X | N/S | 12 | 10 | 1198 | 170 | <4 | <0.3 | 19.83 | 3.39 | N/S | N/S | 346.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-28 | 1.91 | 7.3 | 8.3 | N/S | N/S | N/S | 12 | 10 | 1224 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 358.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-29 | 2.05 | 7.4 | 7.7 | N/S | N/S | N/S | 13 | 11 | 1230 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | 371.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-30 | 2.19 | 7.3 | 7.9 | N/S | N/S | N/S | 14 | 11 | 1176 | 180 | <4 | <0.3 | 18.49 | 3.17 | N/S | N/S | 342.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-01 | 2.31 | 7.2 | 7.8 | T/X | T/X | <5 | 12 | 10 | 1180 | 204 | <4 | <0.3 | 17.11 | 2.78 | <0.005 | <5 | 331.03 | 0.9 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-05-02 | 2.27 | 7.3 | 7.4 | T/X | T/X | N/S | 9 | 9 | 1184 | 188 | <4 | <0.3 | 18.6 | 2.93 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.049 | <0.002 | <0.004 | 0.088 | 0.46 | 0.07 | <0.002 | 0.053 | 0.002 | <0.004 | <0.004 | 0.073 | <0.002 | <0.002 | <0.002 | N/S | 97.66 | 37.53 | 398 | <0.5 | N/S
2023-05-03 | 2.15 | 7.3 | 8.4 | T/X | T/X | N/S | 9 | 9 | 1226 | 216 | <4 | <0.3 | 19.62 | 3.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-04 | 2 | 7.4 | 8.1 | T/X | T/X | N/S | 6 | 5 | 1278 | 212 | <4 | <0.3 | 19.93 | 3.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-05 | 1.95 | 7.4 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1256 | 168 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-06 | 1.93 | 7.5 | 7.5 | N/S | N/S | N/S | <4 | 4 | 1302 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-07 | 1.97 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1222 | 152 | <4 | 0.6 | 19.07 | 3.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-08 | 2.16 | 7.4 | 5.6 | 4 | 3 | <5 | <4 | <4 | 1228 | 160 | <4 | 0.4 | 17.45 | 2.92 | <0.005 | <5 | 362.58 | 0.9 | 2500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-05-09 | 2.03 | 7.4 | 7.7 | 4 | 3 | N/S | 4 | <4 | 1182 | 156 | <4 | 0.3 | 18.01 | 2.79 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.009 | 0.07 | N/S | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | 93.96 | 34.6 | 377 | 1.2 | N/S
2023-05-10 | 1.94 | 7.4 | 7.9 | T/X | T/X | N/S | 25 | 22 | 1162 | 164 | <4 | <0.3 | 19.39 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-11 | 1.98 | 7.3 | 7.5 | T/X | T/X | N/S | 21 | 19 | 1356 | 176 | 3 | 0.4 | 19 | 3.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-12 | 2 | 7.3 | 7.4 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-13 | 2.78 | 7.3 | 7.6 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-14 | 2.28 | 7.3 | 6.6 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-15 | 2.18 | 7.3 | 7.2 | 11 | 6 | <5 | 9 | 9 | 1090 | 168 | <4 | 0.4 | 17.05 | 2.71 | <0.005 | <5 | 278.16 | 0.8 | 7700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-05-16 | 2.35 | 7.3 | 7.4 | 9 | 6 | N/S | 10 | 7 | 1066 | 112 | 1 | 0.9 | 19.08 | 2.93 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.011 | 0.09 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.037 | <0.002 | <0.002 | <0.002 | N/S | 82.88 | 32.8 | 342 | 1.6 | N/S
2023-05-17 | 1.98 | 7.3 | 7.1 | 8 | 5 | N/S | 4 | 6 | 1082 | 134 | <4 | 0.7 | 20.19 | 3.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-18 | 1.83 | 7.3 | 7.3 | 4 | 3 | N/S | <4 | <4 | 1082 | 122 | <4 | 0.6 | 22.04 | 2.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-19 | 2.04 | 7.4 | 5.6 | N/S | N/S | N/S | <4 | <4 | 1040 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-20 | 2.11 | 7.4 | 6.9 | N/S | N/S | N/S | 4 | <4 | 1164 | 226 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-21 | 2.06 | 7.5 | 6.8 | N/S | N/S | N/S | 4 | <4 | 1134 | 152 | <4 | 0.6 | 18.6 | 3.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-22 | 1.99 | 7.2 | 7.4 | T/X | T/X | <5 | <4 | <4 | 1206 | 142 | <4 | 0.5 | 18.1 | 3.27 | <0.005 | <5 | 368.77 | 1 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-05-23 | 1.93 | 7.3 | 7.3 | T/X | T/X | N/S | <4 | <4 | 1174 | 136 | <4 | <0.3 | 19.84 | 3.45 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.006 | 0.05 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | 90.09 | 33.04 | 361 | 0.5 | N/S
2023-05-24 | 2.06 | 7.5 | 6.8 | 17 | 8 | N/S | 6 | 6 | 1128 | 124 | 7 | 1.3 | 15.32 | 3.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-25 | 1.89 | 7.5 | 7.2 | 8 | 4 | N/S | <4 | <4 | 1146 | 150 | <4 | 0.3 | 17.92 | 3.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-26 | 1.83 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1408 | 364 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-27 | 1.92 | 7.4 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1604 | 432 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-28 | 1.83 | 7.4 | 8.3 | N/S | N/S | N/S | 4 | 4 | 1698 | 484 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-29 | 1.92 | 7.4 | 8 | 7 | 3 | <5 | 5 | 4 | 1744 | 462 | <1 | 0.5 | 20.89 | 2 | <0.005 | <5 | 534.43 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-30 | 1.85 | 7.4 | 7.9 | 5 | 4 | N/S | 5 | 4 | 1782 | 508 | <4 | <0.3 | 20.61 | 3.82 | N/S | N/S | N/S | N/S | 3600 | <0.002 | 0.059 | <0.002 | <0.004 | 0.006 | 0.06 | N/S | <0.002 | 0.021 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | <3 | 128.79 | 42.26 | 496 | 0.6 | N/S
2023-05-31 | 1.88 | 7.4 | 7.5 | T/X | T/X | N/S | 5 | 4 | 1690 | 432 | <4 | <0.3 | 21.24 | 3.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-01 | 1.79 | 7.4 | 8.1 | T/X | T/X | N/S | <4 | <4 | 1516 | 292 | <4 | <0.3 | 22.69 | 3.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-02 | 1.98 | 7.4 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1478 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-03 | 1.85 | 7.4 | 6.6 | N/S | N/S | N/S | <4 | <4 | 1478 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-04 | 1.82 | 7.4 | 6.1 | N/S | N/S | N/S | 4 | 5 | 1444 | 310 | <4 | 0.4 | 22.61 | 3.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-05 | 1.82 | 7.4 | 5.2 | 4 | <2 | <5 | <4 | <4 | 1450 | 316 | <4 | <0.3 | 22.38 | 3.66 | <0.005 | <5 | 475.77 | 1 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-06-06 | 1.78 | 7.4 | 6.9 | 5 | 2 | N/S | <4 | <4 | 1536 | 408 | 6 | 0.3 | 21.79 | 3.33 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.052 | <0.002 | <0.004 | 0.007 | 0.07 | 0.06 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.046 | <0.002 | <0.002 | <0.002 | N/S | 115.86 | 41.41 | 460 | 1 | N/S
2023-06-07 | 1.81 | 7.5 | 7 | 13 | 6 | N/S | 8 | 7 | 1382 | 300 | <4 | 0.3 | 22.62 | 3.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-08 | 1.8 | 7.5 | 6 | 17 | 9 | N/S | 8 | 6 | 1510 | 376 | <4 | 0.4 | 20.27 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-09 | 1.71 | 7.3 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1584 | 398 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-10 | 1.69 | 7.3 | 7.5 | N/S | N/S | N/S | 6 | 7 | 1578 | 412 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-11 | 1.88 | 7.3 | 6.6 | N/S | N/S | N/S | 5 | 6 | 1590 | 426 | <4 | 0.8 | 23.73 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-12 | 1.79 | 7.2 | 6.8 | 13 | 4 | <5 | 6 | 4 | 1546 | 472 | <4 | 0.5 | 23.05 | 3.98 | <0.005 | <5 | 434.76 | 1 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S
2023-06-13 | 1.67 | 7.3 | 7.3 | 13 | 6 | N/S | 9 | 7 | 1354 | 254 | <4 | <0.3 | 26.03 | 3.78 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | 100.83 | 36.03 | 400 | 0.7 | N/S
2023-06-14 | 1.97 | 7.2 | 7.3 | 6 | 3 | N/S | 4 | 4 | 1236 | 228 | <4 | <0.3 | 22.17 | 3.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-15 | 2.01 | 7.3 | 7.7 | <2 | <2 | N/S | <4 | <4 | 1232 | 184 | <4 | <0.3 | 23 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-16 | 1.53 | T/X | T/X | N/S | N/S | N/S | <4 | <4 | 1298 | 272 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-17 | 1.99 | 7.5 | 5.9 | N/S | N/S | N/S | <4 | <4 | 1316 | 242 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-18 | 1.72 | 7.5 | 6.2 | N/S | N/S | N/S | <4 | <4 | 1576 | 480 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-19 | 1.9 | 7.5 | 7.4 | 5 | <2 | <5 | 5 | 4 | 1582 | 466 | <4 | 0.4 | 21.26 | 3.9 | <0.005 | <5 | 449.04 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-20 | 1.78 | 7.5 | 6.6 | <2 | <2 | N/S | <4 | <4 | 1616 | 466 | <4 | <0.3 | 23 | 3.76 | N/S | N/S | N/S | N/S | 1000 | <0.002 | 0.053 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | <3 | 123.22 | 40.07 | 473 | <0.5 | N/S
2023-06-21 | 1.86 | 7.4 | 6.8 | 11 | 5 | N/S | 10 | 9 | 1766 | 476 | <4 | <0.3 | 20.31 | 3.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-22 | 1.8 | 7.3 | 7.4 | 26 | 13 | N/S | 23 | 20 | 1802 | 442 | 2 | <0.3 | 20.68 | 3.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-23 | 1.82 | 7.3 | 6.9 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-24 | 1.8 | 7.3 | 7.5 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-25 | 2.29 | 7.2 | 6.7 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-26 | 2.36 | 7.2 | 7 | T/X | T/X | <5 | 21 | 18 | 1378 | 306 | 4 | 0.4 | 16.83 | 2.59 | 0.006 | <5 | 409.04 | 0.7 | 5100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-06-27 | 2.31 | 7.3 | 7.4 | T/X | T/X | N/S | 23 | 18 | 1696 | 354 | 3 | 0.6 | 18.9 | 6.21 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.057 | <0.002 | <0.002 | 0.012 | 0.16 | N/S | <0.002 | 0.035 | <0.002 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | N/S | 114.29 | 39.43 | 448 | 1 | N/S
2023-06-28 | 2.19 | 7.3 | 7.5 | T/X | T/X | N/S | 21 | 17 | 1816 | 374 | 2 | 0.7 | 20.87 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-29 | 1.91 | 7.4 | 7.2 | T/X | T/X | N/S | <4 | <4 | 1840 | 382 | <4 | 0.6 | 21.21 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-30 | 1.9 | 7.4 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1574 | 284 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-01 | 1.89 | 7.4 | 6.4 | N/S | N/S | N/S | 4 | <4 | 1528 | 284 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-02 | 3.14 | 7.4 | 6.7 | N/S | N/S | N/S | 6 | <4 | 968 | 166 | <4 | <0.3 | 15.87 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-03 | 4.08 | 7.2 | 7.1 | T/X | T/X | T/X | 4 | <4 | 796 | 140 | T/X | T/X | T/X | T/X | <0.005 | N/S | 219.56 | 0.5 | 36000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-07-04 | 3.85 | 7.3 | 5.9 | 5 | <2 | N/S | <4 | <4 | 1612 | 772 | 2 | 1.4 | 8.38 | 1.36 | N/S | <5 | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.005 | 0.06 | 0.06 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | 83.63 | 29.71 | 331 | N/S | N/S
2023-07-05 | 3 | 7.4 | 6.7 | T/X | T/X | N/S | 11 | 9 | 1096 | 210 | 2 | 0.6 | 12.38 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 1.3 | N/S
2023-07-06 | 4.1 | 7.2 | 7.2 | 5 | 3 | N/S | 10 | 7 | 776 | 152 | 2 | <0.3 | 9.24 | 1.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-07 | 4.07 | 7.2 | 7.3 | N/S | N/S | N/S | 8 | 6 | 910 | 210 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-08 | 4.1 | 7.2 | 7.4 | N/S | N/S | N/S | 9 | 7 | 954 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-09 | 3.85 | 7.3 | 6.8 | N/S | N/S | N/S | 10 | 8 | 1080 | 290 | 2 | 0.5 | 12.82 | 1.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-10 | 2.74 | 7.3 | 7.1 | 7 | 2 | <5 | 8 | 5 | 1034 | 192 | <4 | 0.4 | 13.86 | 2.14 | <0.005 | <5 | 255.98 | 0.7 | 29000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-07-11 | 2.61 | 7.4 | 7.7 | 5 | 3 | N/S | 8 | 7 | 1010 | 208 | <4 | <0.3 | 18.34 | 2.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.006 | 0.1 | N/S | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | 74.57 | 28.79 | 305 | 1 | N/S
2023-07-12 | 3.91 | 7.3 | 7.4 | 6 | 3 | N/S | 8 | 7 | 768 | 186 | 2 | <0.3 | 10.37 | 1.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-13 | 4.1 | 7.4 | 8.1 | 3 | <2 | N/S | <4 | <4 | 726 | 226 | 2 | <0.3 | 9.01 | 1.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-14 | 4.1 | 7.3 | 8.2 | N/S | N/S | N/S | <4 | <4 | 820 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-15 | 4.1 | 7.4 | 6.3 | N/S | N/S | N/S | <4 | <4 | 938 | 188 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-16 | 4.1 | 7.3 | 7.1 | N/S | N/S | N/S | 6 | 6 | 884 | 164 | 1 | <0.3 | 11.65 | 1.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-17 | 4.1 | 7.4 | 6.1 | 4 | 2 | <5 | <4 | <4 | 884 | 134 | <4 | <0.3 | 12.2 | 1.38 | <0.005 | <5 | 217.42 | 0.6 | 300000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-07-18 | 4.03 | 7.3 | 7.6 | 4 | <2 | N/S | <4 | <4 | 954 | 160 | <4 | <0.3 | 14.18 | 1.62 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 71.82 | 27.48 | 292 | 1.5 | N/S
2023-07-19 | 3.28 | 7.2 | 7.5 | 8 | 3 | N/S | 5 | 5 | 1140 | 218 | <4 | <0.3 | 13.68 | 2.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-20 | 2.08 | 7.4 | 7.7 | 5 | 2 | N/S | 4 | <4 | 1160 | 198 | <4 | <0.3 | 19.81 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-21 | 2.07 | 7.4 | 7.8 | N/S | N/S | N/S | 5 | 4 | 1286 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-22 | 2.06 | 7.4 | 3.9 | N/S | N/S | N/S | 5 | 4 | 1264 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-23 | 2.16 | 7.4 | 5 | N/S | N/S | N/S | 5 | 4 | 1260 | 224 | <4 | 0.6 | 22.68 | 2.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-24 | 2.35 | 7.3 | 7.2 | 8 | 4 | T/X | 5 | 4 | 1358 | 334 | <4 | 1.1 | 19.61 | 2.69 | <0.005 | <5 | 407.77 | 0.8 | 86000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-07-25 | 1.96 | 7.4 | 7.7 | 8 | 3 | N/S | 5 | 4 | 1448 | 396 | <4 | 0.4 | 20.74 | 2.91 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.006 | 0.11 | N/S | <0.002 | 0.011 | 0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 110.85 | 39.06 | 438 | 0.6 | N/S
2023-07-26 | 1.97 | 7.4 | 7.7 | 10 | 4 | N/S | 9 | 7 | 1368 | 244 | 5 | <0.3 | 22.27 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-27 | 1.97 | 7.4 | 7.8 | 7 | 4 | N/S | 4 | <4 | 1322 | 226 | <4 | 1.2 | 22.56 | 3.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-28 | 3.25 | 7.4 | 7.4 | N/S | N/S | N/S | 6 | 5 | 1128 | 286 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-29 | 3.69 | 7.3 | 6.9 | N/S | N/S | N/S | <4 | <4 | 994 | 276 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-30 | 2.02 | 7.4 | 7.3 | N/S | N/S | N/S | 11 | 9 | 1192 | 300 | 2 | 0.4 | 14.05 | 2.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-07-31 | 2.46 | 7.4 | 7.5 | 12 | 6 | <5 | 13 | 10 | 1226 | 232 | 1 | 1.2 | 17.15 | 2.68 | <0.005 | <5 | 350.04 | 0.8 | 6200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-08-01 | 1.99 | 7.4 | 7 | 5 | 6 | N/S | <4 | <4 | 1394 | 390 | 2 | 0.9 | 16.47 | 2.61 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.048 | <0.002 | <0.004 | 0.005 | 0.06 | 0.05 | <0.002 | 0.02 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 106.35 | 36.54 | 416 | 1 | N/S
2023-08-02 | 2.11 | 7.4 | 7.6 | 6 | 3 | N/S | 6 | 4 | 1466 | 388 | <4 | 0.3 | 20.51 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-03 | 2.26 | 7.4 | 7.6 | 6 | 3 | N/S | 7 | 5 | 1260 | 174 | <4 | <0.3 | 22.04 | 2.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-04 | 2.15 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1288 | 262 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-05 | 2.03 | 7.4 | 4.5 | N/S | N/S | N/S | 4 | <4 | 1268 | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-06 | 2.93 | 7.3 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1158 | 238 | <4 | 0.3 | 18.24 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-07 | 2.37 | 7.4 | 7.3 | 14 | 5 | <5 | 12 | 9 | 1090 | 164 | 10 | 0.4 | 14.96 | 2.54 | <0.005 | <5 | 299.74 | 0.8 | 42000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-08-08 | 1.91 | 7.4 | 7.2 | 9 | 4 | N/S | 8 | 7 | 1088 | 118 | <4 | <0.3 | 15.19 | 2.79 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.005 | 0.09 | N/S | <0.002 | 0.028 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 84.92 | 30.26 | 337 | 1 | N/S
2023-08-09 | 1.75 | 7.4 | 7.3 | T/X | T/X | N/S | 7 | 7 | 1128 | 138 | <4 | 0.4 | 15.91 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-10 | 1.55 | 7.4 | 7.2 | T/X | T/X | N/S | 5 | <4 | 1132 | 220 | <4 | <0.3 | 18.26 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-11 | 2.1 | 7.4 | 7.2 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-12 | 1.91 | N/S | N/S | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-13 | 1.78 | N/S | N/S | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-14 | 1.71 | 7.4 | 6.7 | 11 | 5 | <5 | 7 | N/S | 1026 | 204 | <4 | 2 | 14.03 | 3.12 | <0.005 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-08-15 | 2.36 | 7.4 | 6.7 | 6 | 4 | N/S | 5 | 4 | 766 | 186 | 2 | 0.8 | 10 | 1.84 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.004 | 0.07 | N/S | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.015 | <0.002 | <0.002 | <0.002 | N/S | 72.85 | 26.85 | 292 | 1 | N/S
2023-08-16 | 2.29 | 7.4 | 7 | 14 | 6 | N/S | 16 | 13 | 794 | 138 | 3 | 0.8 | 12.19 | 1.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-17 | 2.3 | 7.4 | 6.4 | 15 | 5 | N/S | 18 | 15 | 836 | 122 | <4 | 0.8 | 15.08 | 2.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-18 | 2.5 | 7.4 | 6.8 | N/S | N/S | N/S | 11 | 9 | 952 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-19 | 2.55 | 7.4 | 6.9 | N/S | N/S | N/S | 13 | 12 | 1218 | 282 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-20 | 2.49 | 7.4 | 6.9 | N/S | N/S | N/S | 10 | 10 | 1144 | 238 | <4 | 0.7 | 17.76 | 2.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-21 | 2.45 | 7.4 | 6.6 | T/X | T/X | <5 | <4 | <4 | 1076 | 296 | 6 | 0.6 | 17.73 | 2.49 | 0.006 | <5 | 226.91 | 0.8 | 35000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-08-22 | 3 | 7.4 | 7.4 | T/X | T/X | N/S | 11 | 9 | 1080 | 258 | 4 | 1.5 | 14.96 | 2.82 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.012 | 0.2 | N/S | <0.002 | 0.035 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | 82.79 | 28.77 | 325 | <0.5 | N/S
2023-08-23 | 2.77 | 7.3 | 5.3 | 17 | 5 | N/S | 13 | 11 | 1004 | 168 | 3 | 1.6 | 11.9 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-24 | 2.36 | 7.3 | 6.5 | 4 | <2 | N/S | <4 | <4 | 938 | 156 | <4 | 0.7 | 11.34 | 2.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-25 | 2.54 | 7.3 | 6.4 | N/S | N/S | N/S | <4 | <4 | 1244 | 274 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-26 | 2.62 | 7.3 | 6.1 | N/S | N/S | N/S | <4 | <4 | 1400 | 326 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-27 | 2.37 | 7.3 | 6.4 | N/S | N/S | N/S | <4 | <4 | 1582 | 408 | <4 | 0.8 | 18.47 | 3.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-28 | 2.33 | 7.3 | 6.9 | 5 | 3 | <5 | <4 | <4 | 1434 | 298 | <4 | 0.8 | 14.1 | 3.36 | <0.005 | <5 | 452.24 | 0.9 | 2400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-08-29 | 2.12 | 7.4 | 6.7 | 6 | <2 | N/S | <4 | <4 | 1224 | 252 | <1 | 1 | 8.48 | 3.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.003 | 0.05 | N/S | <0.002 | 0.022 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | 97.05 | 32.2 | 375 | <0.5 | N/S
2023-08-30 | 1.99 | 7.5 | 6.8 | 15 | 5 | N/S | 11 | 9 | 1298 | 222 | 3 | 1.6 | 9.49 | 3.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-08-31 | 1.99 | 7.4 | 6.8 | 12 | 4 | N/S | 8 | 6 | 1460 | 282 | 3 | 1.1 | 14.7 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-01 | 1.96 | 7.4 | 7.2 | N/S | N/S | N/S | 9 | 8 | 1496 | 296 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-02 | 1.88 | 7.4 | 2.9 | N/S | N/S | N/S | 8 | 8 | 1516 | 324 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-03 | 1.88 | 7.5 | 7.2 | N/S | N/S | N/S | 8 | 6 | 1672 | 452 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-04 | 1.93 | 7.4 | 6.8 | 14 | 5 | <5 | 8 | 5 | 1752 | 472 | <4 | 0.7 | 19.43 | 3.52 | <0.005 | <5 | 543.14 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-05 | 1.95 | 7.4 | 7 | 13 | 5 | N/S | 7 | 6 | 1564 | 338 | <4 | 0.7 | 17.75 | 3.45 | N/S | N/S | N/S | N/S | 7600 | <0.002 | 0.055 | <0.002 | <0.004 | 0.007 | 0.1 | 0.05 | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | <3 | 120.44 | 37.92 | 457 | 0.7 | N/S
2023-09-06 | 3.27 | 7.4 | 7.6 | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | S/X | S/X | S/X | N/S | S/X
2023-09-07 | 3.54 | 7.3 | 7 | 14 | 8 | N/S | 5 | 4 | 894 | 174 | 2 | 0.6 | 8.6 | 1.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-08 | 3.07 | 7.3 | 7.3 | N/S | N/S | N/S | <4 | <4 | 998 | 150 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-09 | 1.96 | 7.5 | 6.2 | N/S | N/S | N/S | <4 | <4 | 1254 | 274 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-10 | 2.11 | 7.5 | 6.9 | N/S | N/S | N/S | 4 | <4 | 1288 | 244 | <4 | 0.8 | 19.26 | 2.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-11 | 3.18 | 7.4 | 7.4 | 6 | 3 | <5 | <4 | <4 | 926 | 126 | <4 | 0.6 | 14.08 | 1.89 | <0.005 | <5 | 285.16 | 0.7 | 4200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-09-12 | 4.07 | 7.2 | 7.4 | 6 | 3 | N/S | 5 | 4 | 620 | 92 | 2 | 0.5 | 8.79 | 1.45 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.025 | <0.002 | <0.004 | 0.005 | 0.07 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | 58.19 | 21.37 | 233 | 2.6 | N/S
2023-09-13 | 3.77 | 7.4 | 6.9 | T/X | T/X | N/S | 17 | 13 | 722 | 128 | <4 | 0.4 | 22.48 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-14 | 2.61 | 7.4 | 7.3 | T/X | T/X | N/S | 11 | 8 | 848 | 150 | <4 | 0.4 | 14.57 | 2.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-15 | 2.9 | 7.3 | 7.6 | N/S | N/S | N/S | 7 | 5 | 1060 | 194 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-16 | 2.09 | 7.4 | 7.7 | N/S | N/S | N/S | 7 | 5 | 1070 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-17 | 3.6 | 7.4 | 7.7 | N/S | N/S | N/S | 11 | 9 | 728 | 166 | <4 | 0.3 | 13.17 | 2.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-18 | 4.1 | 7.3 | 7.7 | 7 | 3 | <5 | 10 | 7 | 640 | 96 | 2 | <0.3 | 9.44 | 1.48 | <0.005 | <5 | 144.93 | 0.5 | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-09-19 | 3.95 | 7.3 | 7.6 | 7 | 3 | N/S | 9 | 8 | 728 | 104 | <4 | <0.3 | 11.72 | 1.6 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.006 | 0.1 | N/S | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 70.89 | 26.62 | 287 | 2.5 | N/S
2023-09-20 | 3.73 | 7.3 | 7.7 | T/X | T/X | N/S | 7 | 4 | 770 | 136 | <4 | <0.3 | 14.8 | 1.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-21 | 2.62 | 7.4 | 7.6 | T/X | T/X | N/S | 4 | <4 | 972 | 122 | <4 | 0.5 | 13.35 | 2.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-22 | 3.25 | 7.4 | 7.3 | N/S | N/S | N/S | 4 | <4 | 980 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-23 | 2.25 | 7.5 | 7.1 | N/S | N/S | N/S | <4 | <4 | 954 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-24 | 2.28 | 7.5 | 7.2 | N/S | N/S | N/S | 4 | <4 | 1000 | 186 | <4 | <0.3 | 18.88 | 2.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-25 | 2.83 | 7.4 | 7.1 | 4 | <2 | <5 | 4 | <4 | 936 | 156 | <4 | <0.3 | 17.31 | 2.61 | <0.005 | <5 | 222.81 | 0.8 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-09-26 | 2.27 | 7.5 | 7.3 | 3 | <2 | N/S | <4 | <4 | 876 | 128 | <4 | <0.3 | 18.76 | 2.55 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.004 | 0.05 | N/S | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 74.27 | 28.55 | 303 | 1.2 | N/S
2023-09-27 | 2.31 | 7.5 | 7.8 | T/X | T/X | N/S | 5 | 5 | 888 | 156 | <4 | <0.3 | 20.78 | 2.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-28 | 2.29 | 7.5 | 7.9 | T/X | T/X | N/S | 7 | 5 | 936 | 244 | <4 | <0.3 | 19.89 | 3.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-29 | 2.28 | 7.4 | 7.9 | N/S | N/S | N/S | 5 | 5 | 996 | 168 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-09-30 | 2.14 | 7.4 | 7.8 | N/S | N/S | N/S | 6 | 6 | 1096 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-01 | 2.1 | 7.5 | 7 | N/S | N/S | N/S | <4 | <4 | 1098 | 140 | <4 | <0.3 | 22.25 | 3.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-02 | 2.12 | 7.4 | 7.8 | 6 | 3 | 9 | <4 | <4 | 1114 | 180 | <4 | <0.3 | 19.32 | 3.55 | <0.005 | <5 | 287.82 | 1 | 9900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-10-03 | 1.96 | 7.5 | 7.9 | T/X | T/X | N/S | <4 | <4 | 1282 | 250 | <4 | <0.3 | 20.48 | 3.14 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.004 | 0.06 | 0.04 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | 98.24 | 33.45 | 383 | 1.1 | N/S
2023-10-04 | 1.94 | 7.5 | 7.7 | T/X | T/X | N/S | <4 | <4 | 1294 | 232 | <4 | 0.3 | 20.14 | 3.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-05 | 2.23 | 7.4 | 8.1 | T/X | T/X | N/S | <4 | <4 | 1104 | 156 | <4 | <0.3 | 18.94 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-06 | 2.26 | 7.5 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1002 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-07 | 2.17 | 7.5 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1006 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-08 | 1.99 | 7.6 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1096 | 138 | <4 | 0.4 | 22.8 | 3.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-09 | 1.94 | 7.5 | 7.8 | 4 | 2 | <5 | <4 | <4 | 1044 | 150 | <4 | <0.3 | 22.79 | 3.53 | <0.005 | <5 | 284.29 | 1 | 9300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-10-10 | 1.98 | 7.5 | 7.9 | T/X | T/X | N/S | 4 | <4 | 1022 | 134 | <4 | <0.3 | 21.29 | 2.99 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.004 | 0.05 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | 81.73 | 28.46 | 321 | T/X | N/S
2023-10-11 | 1.91 | 7.5 | 7.9 | T/X | T/X | N/S | 6 | <4 | 1098 | 192 | <4 | <0.3 | 24.09 | 3.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-12 | 3.36 | 7.4 | 8.3 | T/X | T/X | N/S | 5 | 5 | 752 | 120 | <4 | <0.3 | 13.82 | 2.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-13 | 3.63 | 7.3 | 7.6 | N/S | N/S | N/S | <4 | <4 | 774 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-14 | 3.9 | 7.3 | 8 | N/S | N/S | N/S | 4 | <4 | 662 | 102 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-15 | 4.02 | 7.4 | 8.2 | N/S | N/S | N/S | 6 | 5 | 760 | 118 | <4 | <0.3 | 10.57 | 1.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-16 | 3.72 | 7.4 | 7.5 | 6 | 2 | <5 | 6 | 6 | 900 | 134 | <4 | <0.3 | 12.34 | 1.59 | <0.005 | <5 | 229.71 | 0.7 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-10-17 | 2.96 | 7.4 | 7.8 | 6 | 3 | N/S | 5 | 4 | 1022 | 156 | <4 | <0.3 | 16.28 | 1.77 | N/S | N/S | N/S | N/S | N/S | <0.005 | 0.038 | <0.001 | <0.005 | 0.006 | 0.09 | N/S | <0.005 | 0.009 | <0.005 | <0.005 | <0.002 | 0.02 | <0.005 | <0.001 | <0.005 | N/S | 83.4 | 31.82 | 339 | <0.5 | N/S
2023-10-18 | 2.23 | 7.5 | 8 | T/X | T/X | N/S | <4 | <4 | 1086 | 168 | <4 | <0.3 | 19.21 | 2.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-19 | 2.18 | 7.5 | 8.3 | T/X | T/X | N/S | <4 | <4 | 1028 | 124 | <4 | 0.4 | 21.3 | 2.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-20 | 2.88 | 7.5 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1018 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-21 | 2.22 | 7.5 | 8 | N/S | N/S | N/S | <4 | <4 | 1010 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-22 | 2.15 | 7.5 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1030 | 172 | <4 | <0.3 | 20.89 | 0.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-23 | 2.26 | 7.5 | 8.3 | <2 | <2 | 10 | <4 | <4 | 1042 | 146 | <4 | <0.3 | 21.66 | 2.92 | <0.005 | <5 | 251.73 | 0.9 | 3200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-10-24 | 2.04 | 7.5 | 8 | 4 | <2 | N/S | <4 | <4 | 1000 | 140 | <4 | <0.3 | 21.82 | 3.08 | N/S | N/S | N/S | N/S | N/S | <0.005 | 0.034 | <0.001 | <0.005 | 0.012 | 0.07 | N/S | <0.005 | 0.008 | 0.002 | <0.005 | <0.002 | 0.039 | <0.005 | <0.001 | <0.005 | N/S | 80.11 | 30.65 | 326 | <0.5 | N/S
2023-10-25 | 2.21 | 7.5 | 7.8 | T/X | T/X | N/S | 7 | 7 | 912 | 128 | <4 | <0.3 | 21.73 | 2.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-26 | 2.52 | 7.4 | 8 | T/X | T/X | N/S | 6 | 5 | 780 | 126 | <4 | <0.3 | 17.8 | 5.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-27 | 3.77 | 7.3 | 7.6 | N/S | N/S | N/S | 12 | 10 | 738 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-28 | 2.55 | 7.4 | 8.3 | N/S | N/S | N/S | 10 | 8 | 732 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-29 | 2.56 | 7.3 | 8 | N/S | N/S | N/S | 4 | <4 | 1018 | 312 | <4 | <0.3 | 14.06 | 2.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-10-30 | 2.58 | 7.3 | 7.9 | 7 | 3 | 6 | 4 | 5 | 824 | 144 | <4 | <0.3 | 14.97 | 2.31 | 0.005 | <5 | 196.94 | 0.8 | 33000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-10-31 | 2.05 | 7.5 | 8.7 | 6 | <2 | N/S | 5 | 5 | 880 | 158 | <4 | <0.3 | 20.18 | 2.59 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.007 | 0.09 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | 79.53 | 30.91 | 326 | 0.6 | N/S
2023-11-01 | 2.71 | 7.5 | 8.6 | T/X | T/X | N/S | 6 | 4 | 802 | <50 | <4 | 0.3 | 21.04 | 2.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-02 | 2.05 | 7.5 | 8.4 | T/X | T/X | N/S | <4 | <4 | 868 | 150 | <4 | <0.3 | 19.59 | 2.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-03 | 2.01 | 7.5 | 8.5 | N/S | N/S | N/S | <4 | <4 | 938 | 146 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-04 | 2.03 | 7.4 | 8.7 | N/S | N/S | N/S | 6 | 6 | 968 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-05 | 2.34 | 7.5 | 7.8 | N/S | N/S | N/S | 7 | 6 | 958 | 138 | <4 | 0.9 | 20.94 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-06 | 2.41 | 7.4 | 7.2 | 9 | 3 | <5 | <4 | <4 | 1012 | 150 | 2 | 1.3 | 17.08 | 2.8 | 0.007 | <5 | 237.08 | 1 | 670000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-11-07 | 2.01 | 7.5 | 7.9 | 6 | <2 | N/S | 6 | 6 | 978 | 154 | <4 | <0.3 | 20.09 | 2.97 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.007 | 0.09 | 0.03 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.038 | <0.002 | <0.002 | <0.002 | N/S | 92.8 | 34.12 | 372 | <0.5 | N/S
2023-11-08 | 1.99 | 7.5 | 8.2 | T/X | T/X | N/S | 5 | 4 | 1014 | 162 | <4 | <0.3 | 24.39 | 3.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-09 | 1.94 | 7.6 | 7.7 | T/X | T/X | N/S | 5 | <4 | 932 | 150 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-10 | 1.87 | 7.4 | 8.7 | N/S | N/S | N/S | 4 | <4 | 944 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-11 | 1.92 | 7.4 | 8.7 | N/S | N/S | N/S | <4 | <4 | 996 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-12 | 1.96 | 7.4 | 8.6 | N/S | N/S | N/S | 4 | <4 | 1014 | 186 | <4 | <0.3 | 22.62 | 3.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-13 | 1.98 | 7.3 | 8.6 | 4 | <2 | <5 | <4 | <4 | 904 | 128 | <4 | <0.3 | 24.32 | 3.16 | 0.006 | <5 | 199.9 | 1 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-11-14 | 1.86 | 7.5 | 8.4 | 9 | <2 | N/S | 5 | 4 | 968 | 186 | <4 | <0.3 | 23.61 | 3 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.007 | 0.09 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | 90.76 | 30.53 | 352 | 0.5 | N/S
2023-11-15 | 1.82 | 7.5 | 8.2 | T/X | T/X | N/S | <4 | <4 | 914 | 150 | <4 | <0.3 | 25.02 | 3.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-16 | 1.82 | 7.5 | 8.2 | T/X | T/X | N/S | 6 | 4 | 862 | 128 | <4 | <0.3 | 25.23 | 3.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-17 | 1.82 | 7.5 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1040 | 300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-18 | 1.8 | 7.6 | 8.1 | N/S | N/S | N/S | <4 | <4 | 894 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-19 | 1.85 | 7.6 | 7.4 | N/S | N/S | N/S | <4 | <4 | 806 | 132 | <4 | <0.3 | 18.98 | 3.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-20 | 1.88 | 7.5 | 8 | T/X | T/X | <5 | <4 | <4 | 828 | 146 | <4 | <0.3 | 21.69 | 3.57 | 0.006 | <5 | 156.61 | 1 | 27000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-11-21 | 3.5 | 7.3 | 8.5 | T/X | T/X | N/S | 18 | 14 | 668 | 136 | 2 | <0.3 | 14.02 | 2.55 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.026 | <0.002 | <0.004 | 0.01 | 0.12 | N/S | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 60.33 | 22.63 | 244 | 0.7 | N/S
2023-11-22 | 2.51 | 7.4 | 7.9 | T/X | T/X | N/S | 5 | 4 | 728 | 116 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-23 | 2.12 | 7.4 | 8.3 | T/X | T/X | N/S | 5 | 4 | 844 | 142 | <4 | <0.3 | 17.78 | 2.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-24 | 2.13 | 7.5 | 8.6 | N/S | N/S | N/S | 6 | 5 | 884 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-25 | 2.12 | 7.4 | 8.6 | N/S | N/S | N/S | 7 | 6 | 864 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-26 | 2.13 | 7.3 | 8.5 | N/S | N/S | N/S | 8 | 6 | 968 | 240 | <4 | <0.3 | 20.82 | 3.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-27 | 2.29 | 7.4 | 8.4 | 4 | 2 | <5 | 6 | 5 | 978 | 172 | <4 | <0.3 | 22.56 | 3.29 | 0.006 | <5 | 213.74 | 0.9 | 18000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-11-28 | 1.98 | 7.4 | 8.4 | 4 | 3 | N/S | 9 | 8 | 934 | 184 | <4 | <0.3 | 22.05 | 3.25 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.008 | 0.09 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | 77.74 | 29.34 | 315 | 0.8 | N/S
2023-11-29 | 1.89 | 7.5 | 8.7 | 8 | 4 | N/S | 4 | <4 | 882 | 158 | <4 | <0.3 | 23.01 | 3.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-11-30 | 1.93 | 7.5 | 8.4 | 4 | 3 | N/S | <4 | <4 | 876 | 146 | <4 | <0.3 | 24.48 | 3.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-01 | 3.29 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 808 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | 164.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-02 | 4.03 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 656 | 86 | N/S | N/S | N/S | N/S | N/S | N/S | 154.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-03 | 4 | 7.4 | 7.3 | N/S | N/S | N/S | <4 | <4 | 720 | 102 | <4 | <0.3 | 9.83 | 1.33 | N/S | N/S | 147.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-04 | 3.91 | 7.4 | 7.8 | 3 | <2 | <5 | <4 | <4 | 736 | 130 | <4 | <0.3 | 9.36 | 1.45 | <0.005 | <5 | 152.37 | 0.7 | 27000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-12-05 | 2.67 | 7.6 | 7.8 | 2 | <2 | N/S | 6 | 5 | 764 | 134 | <4 | <0.3 | 12.37 | 1.84 | N/S | N/S | 178.94 | N/S | N/S | <0.002 | 0.03 | <0.002 | <0.004 | 0.005 | 0.07 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | 74.92 | 30.65 | 313 | <0.5 | N/S
2023-12-06 | 2.6 | 7.4 | 8.2 | <2 | 4 | N/S | 6 | <4 | 830 | 162 | <4 | <0.3 | 12.35 | 2.06 | N/S | N/S | 183.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-07 | 2.98 | 7.6 | 8.6 | 6 | 3 | N/S | 6 | 5 | 838 | 178 | <4 | 0.4 | 15.14 | 2.22 | N/S | N/S | 175.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-08 | 2.1 | 7.4 | 8 | N/S | N/S | N/S | 6 | 5 | 936 | 226 | N/S | N/S | N/S | N/S | N/S | N/S | 183.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-09 | 2.91 | 7.4 | 8.5 | N/S | N/S | N/S | 6 | 4 | 908 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | 174.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-10 | 2.35 | 7.4 | 7.9 | N/S | N/S | N/S | 6 | 4 | 882 | 166 | <4 | <0.3 | 15.73 | 2.47 | N/S | N/S | 175.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-11 | 2.31 | 7.3 | 8.6 | 6 | 3 | <5 | 5 | 4 | 830 | 100 | <4 | <0.3 | 17.72 | 2.64 | 0.006 | <5 | 170.86 | 0.8 | 9400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-12-12 | 2.47 | 7.4 | 7.8 | 3 | 3 | N/S | 7 | 5 | 840 | 124 | <4 | <0.3 | 18.31 | 2.69 | N/S | N/S | 190.21 | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | 82.45 | 33.33 | 343 | 0.8 | N/S
2023-12-13 | 2.12 | 7.5 | 9 | 6 | 2 | N/S | 5 | 4 | 886 | 134 | <4 | <0.3 | 21.29 | 14.29 | N/S | N/S | 93.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-14 | 2.13 | 7.4 | 9.1 | <2 | 2 | N/S | 6 | 5 | 878 | 156 | <4 | <0.3 | 24.12 | 3.03 | N/S | N/S | 170.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-15 | 2.13 | 7.3 | 8.9 | N/S | N/S | N/S | 5 | 5 | 876 | 120 | N/S | N/S | N/S | N/S | N/S | N/S | 168.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-16 | 2.76 | 7.3 | 3.2 | N/S | N/S | N/S | 9 | 9 | 792 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | 200.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-17 | 4 | 7.3 | 3.2 | N/S | N/S | N/S | 11 | 9 | 862 | 182 | 1 | 0.3 | 11.57 | 1.81 | N/S | N/S | 173.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-18 | 3.24 | 7.2 | 2.9 | 9 | 5 | <5 | 7 | 5 | 942 | 110 | <4 | <0.3 | 12.69 | 2 | 0.006 | <5 | 248.35 | 0.7 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2023-12-19 | 2.2 | 7.5 | 8.6 | 13 | 7 | N/S | 12 | 10 | 1014 | 146 | <4 | <0.3 | 15.25 | 2.34 | N/S | N/S | 281.46 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.009 | 0.1 | N/S | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | 92.93 | 35.25 | 377 | <0.5 | N/S
2023-12-20 | 2.59 | 7.3 | 7.5 | 11 | 5 | N/S | 10 | 9 | 1096 | 158 | <4 | <0.3 | 17.21 | 2.43 | N/S | N/S | 310.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-21 | 2.14 | 7.4 | 8.8 | 9 | 3 | N/S | 10 | 8 | 1086 | 154 | <1 | <0.3 | 19.52 | 2.68 | N/S | N/S | 284.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-22 | 2.62 | 7.4 | 8.7 | N/S | N/S | N/S | 10 | 8 | 1000 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 263.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-23 | 4.1 | 7.1 | 7.3 | N/S | N/S | N/S | 12 | 10 | 754 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 189.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-24 | 4.06 | 7.2 | 7.8 | N/S | N/S | N/S | 12 | 9 | 830 | 104 | T/X | T/X | T/X | T/X | N/S | N/S | 212.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-25 | 3.8 | 7.3 | 7.5 | T/X | T/X | <5 | 10 | 7 | 878 | 138 | 2 | 1.3 | 8.38 | 2.06 | 0.007 | <5 | 217.29 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-26 | 4.1 | 7.4 | 8.7 | T/X | T/X | N/S | 9 | 8 | 744 | 128 | 1 | <0.3 | 8.68 | 1.36 | N/S | N/S | 158.62 | N/S | 17000 | <0.002 | 0.027 | <0.002 | <0.004 | 0.007 | 0.07 | N/S | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.012 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | <0.5 | N/S
2023-12-27 | 4.09 | 7.3 | 8.2 | 4 | <2 | N/S | <4 | <4 | 822 | 134 | <4 | <0.3 | 10.28 | 1.37 | N/S | N/S | 218.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-28 | 3.84 | 7.3 | 7.9 | 4 | <2 | N/S | 4 | <4 | 940 | 132 | <4 | 0.5 | 9.96 | 1.65 | N/S | N/S | 251.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-29 | 3.32 | 7.4 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1012 | 208 | N/S | N/S | N/S | N/S | N/S | N/S | 241.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-30 | 3.09 | 7.4 | 7.5 | N/S | N/S | N/S | <4 | <4 | 900 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 246.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-12-31 | 2.76 | 7.6 | 7.2 | N/S | N/S | N/S | 4 | 4 | 958 | 132 | T/X | T/X | T/X | T/X | N/S | N/S | 256.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
RL effective 1/1/23 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 25 | 1 | 0.3 | 0.5 | 0.15 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
Observations | 365 | 362 | 362 | 146 | 146 | 50 | 353 | 352 | 353 | 353 | 243 | 243 | 243 | 243 | 52 | 52 | 180 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 0
Minimum | 1.53 | 7 | 2.9 | <2 | <2 | <5 | <4 | <4 | 620 | <50 | <1 | <0.3 | 8.38 | 0.76 | <0.005 | <5 | 93.27 | 0.5 | 1000 | <0.002 | 0.025 | <0.002 | <0.002 | 0.003 | 0.04 | 0.03 | <0.002 | 0.003 | <0.002 | <0.004 | <0.002 | 0.012 | <0.002 | <0.001 | <0.002 | <3 | 58.19 | 21.37 | 233 | <0.5
Mean | 2.58 | 7.4 | 7.7752 | <8 | <4 | <4 | <7 | <6 | 1117 | <196 | <3 | <0.4 | 17.08 | 2.69 | <0.004 | <4 | 326.1 | 0.78158 | GM= 11087 | <0.001 | 0.039 | <0.001 | <0.003 | 0.009 | 0.093846 | 0.052222 | <0.001 | 0.013 | <0.001 | <0.003 | <0.003 | 0.030256 | <0.001 | <0.001 | <0.001 | <2 | 89.15 | 33.1 | 359 | <0.9
Maximum | 7.78 | 7.6 | 10.1 | 26 | 13 | 10 | 34 | 29 | 1840 | 772 | 10 | 2.5 | 26.03 | 14.29 | 0.007 | <5 | 718.95 | 1 | 670000 | <0.005 | 0.059 | <0.002 | <0.005 | 0.088 | 0.46 | 0.07 | <0.005 | 0.053 | <0.005 | <0.005 | <0.004 | 0.073 | <0.005 | <0.002 | <0.005 | <3 | 128.79 | 42.97 | 496 | 2.6
%>400=100
January 1, 15, 2023, P-TOT, TKN, NO2+NO3_N, NH3_N, T/X; Aliquot not preserved within holding time.
January 4, 2023, TKN, NO2+NO3_N; Sample MS/MSD recovery failed but LCS passed.
January 10, 11, 2023, TKN: Sample MS/MSD, recovery failed but LCS passed.
January 16, 2023, Phenol; Sample MS/MSD recovery failed but LCS passed.
January 23, 2023, Various analyses, S/X; Cancelled per M&O due to erratic flow at sample point.
January 24, 2023, TP, TKN; Sample MS/MSD recovery failed but LCS passed.
February 2, 13, 14, 2023, TKN; Sample MS/MSD recovery failed but LCS passed.
February 8, 20, 21, 2023, BOD5, CBOD5, T/X; GGA failure.
February 9, 2023, Various analyses, S/X; Cancelled per M&O.
February 12, 19, 2023, P-TOT, TKN, NO2+NO3_N, NH3_N, T/X; Aliquot not preserved within holding time.
February 26, 2023, TP; Sample MS/MSD recovery failed but LCS passed.
March 2, 6, 2023, NO2+NO3_N; Sample MS/MSD recovery failed but LCS passed.
March 9, 13, 15, 28, 2023, TKN; Sample MS/MSD recovery failed but LCS passed.
March 12, 16, 20, 26, 2023, TP, TKN; Sample MS/MSD recovery failed but LCS passed.
March 19, 2023, NH3_N; Sample MS/MSD recovery failed but LCS passed.
March 23, 2023, TP; Sample MS/MSD recovery failed but LCS passed.
April 5, 6, 17, 18, 19, 20, 26, 27, 2023, BOD5, CBOD5, T/X: GGA failure.
April 6, 30, 2023, TKN: Sample MS/MSD recovery failed but LCS passed.
April 11, 18, 27, 2023, TP: Sample MS/MSD recovery failed but LCS passed.
April 11, 2023, Ag: Sample MS recovery failed but LCS passed.
April 26, 2023, NO2+NO3-N: Sample MS/MSD recovery failed but LCS passed.
May 1, 2, 3, 4, 10, 11, 2023, BOD5, CBOD5, T/X: Incubator failure.
May 2, 2023, TKN, As, Ba, Cd, Cr, Cu, Fe, Pb, Mn, Ni, Se, Ag, Zn, Sb, Be, Tl: Sample MS/MSD recovery failed but LCS passed.
May 7, 9, 29, 2023, TKN: Sample MS/MSD recovery failed but LCS passed.
May 8, 2023, NO2+NO3-N: Spike failed but QA passed; parent results qualified.
May 12, 13, 14, 2023, Various analyses, S/X: Sample not representative; cancelled per M&O
May 17, 2023, TP: Spike failed but QA passed; parent results qualified.
May 22, 23, 31, 2023, BOD5, CBOD5, T/X: GGA failure.
May 28, 2023, TKN, NH3-N, NO2+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
May 29, 2023, Cl: Sample MS/MSD recovery failed but LCS passed.
June 1, 2023, BOD5, CBOD5, T/X: GGA failure.
June 1, 5, 7, 8, 14, 15, 20, 28, 29, 2023, TKN, Sample MS/MSD recovery failed but LCS passed.
June 4, 19, 2023, NO2+NO3-N: Sample MS/MSD recovery failed but LCS passed.
June 6, 11, 15, 2023, TP: Sample MS/MSD recovery failed but LCS passed.
June 12, 2023, Cr6+, T/X: Filtered LCS and CCV failure.
June 15, 2023, TP: LIMS used wrong result for duplicate calculation; duplicate passed and parent results qualified.
June 16, 2023, pH, DO, T/X: Power outage at the Lemont plant.
June 18, 2023, TKN, NH3-N, NO2+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
June 23, 24, 25, 2023, Various analyses, S/X: Cancelled per M&O due to an issue with the sample pump flow to the outfall composite sampler.
June 26, 27, 28, 29, 2023, BOD5, CBOD5, T/X: Incubator failure.
July 3, 5, 2023, BOD5, CBOD5, T/X: Test cancelled due to incubator failure, no rerun due to hold time.
July 3, 2023, P-TOT, TKN, NO2-N+NO3-N, NH3-N, T/X: Sample aliquot not preserved within required holding time due to holiday.
July 3, 2023, FOG, T/X: LCS failure.
July 4, 2023, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
July 5, 2023, NH3-N, TKN: Sample MS/MSD recovery failed but LCS passed.
July 16, 2023, NH3-N, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
July 17, 2023, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
July 24, 2023, FOG, T/X: Sample aliquot could not be located.
July 27, 2023, NH3-N, TP: Sample MS/MSD recovery failed but LCS passed.
August 9, 10, 21, 22, 2023, BOD5, CBOD5, T/X: Blank failure.
August 11, 12, 13, 2023, BOD5, CBOD5, SS, VSS, TS, TVS, TKN, NH3-N, NO2-N+NO3-N, P-TOT, pH, S/X: Sample pump was turned off to avoid dry-pumping.
August 12, 13, 2023, D.O., pH, T/X: Sample pump turned off to avoid dry pumping.
August 14, 27, 2023, P-TOT: Sample MS/MSD recovery failed but LCS passed.
August 29, 30, 2023, TKN: Sample MS/MSD recovery failed but LCS passed.
September 3, 2023, P-TOT, TKN, NO2-N+NO3-N, NH3-N, T/X: Sample aliquot was not preserved within required holding time due to holiday.
September 6, 2023, SS, VSS, TS, TVS, BOD5, CBOD5, P-TOT, NH3-N, NO2-N+NO3-N, TKN, pH, S/X:Sample was non-representative, per M&O.
September 12, 2023, P-TOT, TKN: Sample MS/MSD recovery failed but LCS passed.
September 13, 14, 20, 21, 27, 28, 2023, BOD5, CBOD5, T/X: Incubator failure.
September 25, 28, 2023, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
October 3, 10, 2023, BOD5, CBOD5, T/X: LCS failed.
October 4, 5, 11, 12, 18, 19, 25, 26, 2023, BOD5, CBOD5, T/X: Incubator failure.
October 5, 17, 22, 26, 31, 2023, TP: Sample MS/MSD recovery failed but LCS passed.
October 10, 2023, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
October 10, 2023 Hg LL, T/X: Field blank is greater than the LOQ.
October 17, 24, 2023, As, Ba, Cd, Cr, Cu, Fe, Pb, Mn, Ni, Se, Ag, Zn, Sb, Be, Tl: Results were provided by an outside lab.
November 1, 2, 8, 9, 2023, BOD5, CBOD5, T/X: Incubator failure.
November 5, 16, 28, 2023, TP: Sample MS/MSD recovery failed but LCS passed.
November 6, 2023, TKN: Sample MS/MSD recovery failed but LCS passed.
November 9, 2023, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot was not preserved within required holding time due to holiday.
November 12, 13, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
November 15, 16, 20, 21, 22, 23, 2023, BOD5, CBOD5, T/X: Blank failure.
November 22, 2023, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within holding time specifications.
December 7, 21, 2023, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
December 13, 2023, TP: Sample MS/MSD recovery failed but LCS passed.
December 24, 31, 2023, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within holding time specifications.
December 25, 26, 2023, BOD5, CBOD5, T/X: GGA failure.
December 26, 2023, TKN: Sample MS/MSD recovery failed but LCS passed.

## Lemont Outfall 2024
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2024-01-01 | 2.51 | 7.4 | 7.5 | <2 | <2 | <5 | 4 | <4 | 1082 | 186 | <4 | 0.3 | 13.81 | 1.75 | 0.008 | <5 | 269.19 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-02 | 2.71 | 7.5 | 9.1 | <2 | 3 | N/S | 12 | 10 | 1034 | 146 | 6 | 0.9 | 16.12 | 2.55 | N/S | N/S | 271.02 | N/S | 8900 | <0.002 | 0.036 | <0.002 | <0.004 | 0.008 | 0.09 | 0.04 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | <0.5 | N/S
2024-01-03 | 2.29 | 7.4 | 7.8 | 11 | 4 | N/S | 10 | 7 | 1056 | 146 | <4 | 0.6 | 14.85 | 2.46 | N/S | N/S | 282.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-04 | 2.17 | 7.5 | 8.9 | 3 | 3 | N/S | 7 | 6 | 1048 | 136 | <4 | <0.3 | 16.83 | 2.58 | N/S | N/S | 286.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-05 | 2.47 | 7.4 | 8.7 | N/S | N/S | N/S | 7 | 5 | 1080 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 302.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-06 | 2.12 | 7.4 | 8.7 | N/S | N/S | N/S | 9 | 7 | 1364 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 478.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-07 | 2.18 | 7.4 | 8.8 | N/S | N/S | N/S | 13 | 10 | 1494 | 152 | <4 | <0.3 | 18.07 | 2.56 | N/S | N/S | 560.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-08 | 2.87 | 7.4 | 9.1 | T/X | T/X | <5 | 12 | 11 | 1372 | 234 | <4 | 0.7 | 15.04 | 2.62 | 0.009 | <5 | 450.27 | 0.8 | 39000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S
2024-01-09 | 3.29 | 7.3 | 7.7 | T/X | T/X | N/S | 4 | 4 | 2114 | 122 | 2 | 0.6 | 10.82 | 2.18 | N/S | N/S | 1029.04 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.005 | 0.06 | N/S | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2024-01-10 | 4.08 | 7.2 | 8.9 | T/X | T/X | N/S | 11 | 10 | 2046 | 172 | 2 | 0.5 | 9.86 | 1.43 | N/S | N/S | 1042.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-11 | 4.1 | 7.2 | 9 | T/X | T/X | N/S | 8 | 6 | 1506 | 222 | 1 | <0.3 | 11.52 | 1.43 | N/S | N/S | 678.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-12 | 4.08 | 7.3 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1190 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 677.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-13 | 4.1 | 7.5 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1462 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | 568.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-14 | 4.1 | 7.3 | 9.8 | N/S | N/S | N/S | <4 | <4 | 1248 | 122 | T/X | T/X | T/X | T/X | N/S | N/S | 530.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-15 | 4.06 | 7.5 | 8.6 | 7 | 3 | <5 | 7 | 6 | 1154 | 132 | <4 | <0.3 | 15.65 | 1.54 | 0.006 | <5 | 431.4 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-16 | 3.75 | 7.3 | 8.7 | 7 | 2 | N/S | 8 | 6 | 1178 | 192 | <4 | <0.3 | 13.71 | 1.68 | N/S | N/S | 399.11 | N/S | 2600 | <0.002 | 0.04 | <0.002 | <0.004 | 0.006 | 0.08 | N/S | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 0.8 | N/S
2024-01-17 | 3.5 | 7.3 | 8.8 | T/X | T/X | N/S | 8 | 8 | 1130 | 156 | <4 | <0.3 | 14.64 | 1.88 | N/S | N/S | 371.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-18 | 2.22 | 7.4 | 9.2 | T/X | T/X | N/S | 8 | 6 | 1078 | 186 | 2 | <0.3 | 16.28 | 2.16 | N/S | N/S | 330.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-19 | 2.96 | 7.5 | 9.7 | N/S | N/S | N/S | 8 | 7 | 1152 | 144 | N/S | N/S | N/S | N/S | N/S | N/S | 344.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-20 | 2.16 | 7.4 | 8.7 | N/S | N/S | N/S | 10 | 8 | 1336 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | 420.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-21 | 2.79 | 7.4 | 9.8 | N/S | N/S | N/S | 7 | 6 | 1212 | 114 | 2 | 1.8 | 16.76 | 2.47 | N/S | N/S | 384.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-22 | 2.16 | 7.4 | 8.3 | 8 | 5 | <5 | 6 | 4 | 1394 | 156 | <4 | <0.3 | 17.91 | 2.5 | <0.005 | <5 | 476.33 | 0.9 | 8700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-01-23 | 3.3 | 7.5 | 9.4 | 14 | 10 | N/S | 18 | 14 | 2732 | 240 | 2 | <0.3 | 14.7 | 2.47 | N/S | N/S | 1309.61 | N/S | N/S | <0.002 | 0.058 | <0.002 | <0.004 | 0.012 | 0.18 | N/S | <0.002 | 0.027 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-01-24 | 3.88 | 7.2 | 9 | 7 | 4 | N/S | 9 | 7 | 2534 | 238 | <4 | <0.3 | 11.1 | 1.5 | N/S | N/S | 1231.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-25 | 4.05 | 7.2 | 9.4 | 10 | 5 | N/S | 9 | 7 | 1902 | 234 | 1 | <0.3 | 8.28 | 1.05 | N/S | N/S | 884.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-26 | 4.09 | 7.3 | 9.5 | N/S | N/S | N/S | <4 | <4 | 1326 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 566.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-27 | 4.1 | 7.6 | 9.5 | N/S | N/S | N/S | <4 | <4 | 1334 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | 547.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-28 | 4.1 | 7.6 | 9.1 | N/S | N/S | N/S | 8 | 6 | 1266 | 166 | <4 | <0.3 | 9.94 | 0.9 | N/S | N/S | 537.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-01-29 | 4.1 | 7.4 | 9.4 | 3 | <2 | <5 | 4 | <4 | 1278 | 154 | <4 | <0.3 | 9.3 | 0.95 | <0.005 | <5 | 524.89 | 0.6 | 5100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-01-30 | 4.1 | 7.3 | 9.3 | 4 | 2 | N/S | 5 | 4 | 1234 | 148 | <4 | <0.3 | 10.41 | 1.13 | N/S | N/S | 514.21 | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.006 | 0.05 | N/S | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2024-01-31 | 4.1 | 7.4 | 8.7 | 8 | 3 | N/S | 7 | 5 | 1240 | 148 | <4 | <0.3 | 11.73 | 1.17 | N/S | N/S | 455.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-01 | 4.1 | 7.4 | 9.5 | 8 | 4 | N/S | 8 | 7 | 1210 | 102 | <4 | <0.3 | 11.8 | 1.3 | N/S | N/S | 466.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-02 | 4.1 | 7.3 | 9.2 | N/S | N/S | N/S | 6 | 5 | 1466 | 318 | N/S | N/S | N/S | N/S | N/S | N/S | 471.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-03 | 4.06 | 7.3 | 9 | N/S | N/S | N/S | 4 | 4 | 1306 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | 464.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-04 | 3.76 | 7.3 | 8.2 | N/S | N/S | N/S | 4 | <4 | 1272 | 188 | <4 | 0.6 | 11.73 | 1.87 | N/S | N/S | 402.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-05 | 3.61 | 7.3 | 8.4 | 6 | 3 | <5 | <4 | <4 | 1238 | 250 | 2 | 0.8 | 11.22 | 2.08 | <0.005 | <5 | 380.91 | 0.7 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-02-06 | 2.98 | 7.4 | 8.5 | 11 | 4 | N/S | 8 | 5 | 1182 | 180 | <4 | 0.3 | 11.71 | 2.07 | N/S | N/S | 389.36 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.007 | 0.07 | 0.04 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2024-02-07 | 2.32 | 7.4 | 8.8 | 7 | 3 | N/S | <4 | <4 | 1214 | 204 | <4 | <0.3 | 16.5 | 2.23 | N/S | N/S | 374.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-08 | 2.41 | 7.4 | 9.1 | 10 | 4 | N/S | 8 | 5 | 1334 | 308 | 9 | 1.4 | 17.44 | 2.65 | N/S | N/S | 343.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-09 | 2.59 | 7.3 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1136 | 174 | N/S | N/S | N/S | N/S | N/S | N/S | 339.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-10 | 2.58 | 7.6 | 8.9 | N/S | N/S | N/S | <4 | <4 | 1152 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | 343.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-11 | 2.27 | 7.4 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1190 | 170 | T/X | T/X | T/X | T/X | N/S | N/S | 337.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-12 | 2.07 | 7.5 | 8.8 | 10 | 5 | <5 | 6 | 4 | 1074 | 114 | <4 | 0.5 | 19.95 | 2.59 | <0.005 | <5 | 306.69 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-13 | 2.51 | 7.4 | 8.9 | 7 | 3 | N/S | <4 | <4 | 1096 | 228 | <4 | 0.7 | 17.34 | 2.48 | N/S | N/S | 308.5 | N/S | 21000 | <0.002 | 0.037 | <0.002 | <0.004 | 0.007 | 0.06 | 0.05 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 0.8 | N/S
2024-02-14 | 2.23 | 7.4 | 8.2 | T/X | T/X | N/S | 5 | 4 | 1028 | 210 | 2 | 0.7 | 16.56 | 2.57 | N/S | N/S | 300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-15 | 1.99 | 7.4 | 8.9 | T/X | T/X | N/S | 5 | <4 | 1046 | 82 | <4 | <0.3 | 20.17 | 2.56 | N/S | N/S | 292.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-16 | 2.38 | 7.4 | 9.1 | N/S | N/S | N/S | 7 | 6 | 1106 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | 287.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-17 | 2.19 | 7.3 | 7.5 | N/S | N/S | N/S | 13 | 12 | 1186 | 240 | N/S | N/S | N/S | N/S | N/S | N/S | 293.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-18 | 1.94 | 7.4 | 8.7 | N/S | N/S | N/S | 9 | 9 | 1068 | 144 | T/X | T/X | T/X | T/X | N/S | N/S | 274.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-19 | 2.43 | 7.4 | 8.8 | T/X | T/X | <5 | 10 | 8 | 1030 | 144 | 4 | 1.1 | 17.22 | 2.62 | <0.005 | <5 | 260.56 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-20 | 2.09 | 7.4 | 7.5 | T/X | T/X | N/S | 7 | 7 | 1006 | 110 | 3 | 1.5 | 14.11 | 2.78 | N/S | N/S | 260.85 | N/S | 540000 | <0.002 | 0.034 | <0.002 | <0.004 | 0.012 | 0.09 | 0.06 | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.044 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 2.2 | N/S
2024-02-21 | 1.88 | 7.4 | 8.9 | 13 | 5 | N/S | <4 | <4 | 1114 | 180 | <4 | <0.3 | 17.17 | 0.56 | N/S | N/S | 266.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-22 | 2.08 | 7.5 | 9.1 | 16 | 7 | N/S | <4 | <4 | 1200 | 168 | <4 | 0.4 | 17.61 | 2.45 | N/S | N/S | 323.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-23 | 2.24 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1312 | 194 | N/S | N/S | N/S | N/S | N/S | N/S | 391.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-24 | 1.86 | 7.6 | 8.8 | N/S | N/S | N/S | <4 | <4 | 1206 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | 336.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-25 | 2.66 | 7.6 | 9.1 | N/S | N/S | N/S | <4 | <4 | 1058 | 98 | <4 | 1.6 | 17.49 | 2.66 | N/S | N/S | 290.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-26 | 1.88 | 7.3 | 8.2 | T/X | T/X | <5 | <4 | <4 | 1046 | 178 | 6 | 0.6 | 14.78 | 2.93 | <0.005 | <5 | 248.87 | 0.9 | 8800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-02-27 | 2.22 | 7.4 | 8.8 | T/X | T/X | N/S | 4 | 4 | 1112 | 186 | <4 | <0.3 | 16.22 | 2.76 | N/S | N/S | 308.84 | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.005 | 0.05 | 0.04 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2024-02-28 | 2.12 | 7.5 | 9 | 4 | 2 | N/S | <4 | <4 | 1192 | 218 | <4 | <0.3 | 17.48 | 2.74 | N/S | N/S | 320.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-02-29 | 2.4 | 7.3 | 8.9 | 6 | 2 | N/S | <4 | <4 | 1422 | 304 | <4 | <0.3 | 19.09 | 2.62 | N/S | N/S | 408.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-01 | 1.74 | 7.4 | 9.5 | N/S | N/S | N/S | <4 | <4 | 1212 | 182 | N/S | N/S | N/S | N/S | N/S | N/S | 362.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-02 | 2.3 | 7.5 | 9.4 | N/S | N/S | N/S | <4 | <4 | 1162 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 350.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-03 | 2 | 7.3 | 8.5 | N/S | N/S | N/S | T/X | T/X | 1280 | 210 | 4 | 0.4 | 17.7 | 2.94 | N/S | N/S | 345.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-04 | 2.01 | 7.5 | 8.9 | 7 | 3 | <5 | <4 | 5 | 1168 | 200 | <4 | <0.3 | 21.46 | 3.4 | <0.005 | <5 | 312.55 | 0.9 | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-03-05 | 3.73 | 7.4 | 9.2 | 17 | 7 | N/S | 27 | 23 | 1010 | 210 | 6 | <0.3 | 14.15 | 2.88 | N/S | N/S | 300.9 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.024 | 0.42 | 0.04 | 0.05 | 0.039 | 0.003 | <0.004 | <0.004 | 0.049 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-03-06 | 3.6 | 7.3 | 9.6 | 8 | 4 | N/S | 5 | 4 | 946 | 168 | <4 | <0.3 | 11 | 1.42 | N/S | N/S | 286.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-07 | 3.38 | 7.3 | 9.4 | 8 | 4 | N/S | 4 | <4 | 976 | 106 | <4 | <0.3 | 12.73 | 1.61 | N/S | N/S | 308.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-08 | 3.61 | 7.4 | 9.2 | N/S | N/S | N/S | <4 | <4 | 1136 | 220 | N/S | N/S | N/S | N/S | N/S | N/S | 294.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-09 | 4.1 | 7.5 | 8.8 | N/S | N/S | N/S | <4 | <4 | 832 | 146 | N/S | N/S | N/S | N/S | N/S | N/S | 236.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-10 | 3.57 | 7.6 | 8.8 | N/S | N/S | N/S | <4 | <4 | 1014 | 182 | <4 | <0.3 | 10.55 | 0.68 | N/S | N/S | 301.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-11 | 3.54 | 7.5 | 8.8 | 4 | <2 | <5 | <4 | <4 | 1096 | 214 | <4 | <0.3 | 11.81 | 1.46 | <0.005 | <5 | 312.29 | 0.6 | 68000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S
2024-03-12 | 3.73 | 7.4 | 9.1 | 8 | 5 | N/S | 6 | 5 | 1074 | 182 | <4 | <0.3 | 12.01 | 1.47 | N/S | N/S | 311.3 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.005 | 0.07 | 0.04 | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.016 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.6 | N/S
2024-03-13 | 3.71 | 7.4 | 8.9 | 9 | 4 | N/S | 7 | 6 | 1068 | 166 | 2 | <0.3 | 13.53 | 1.77 | N/S | N/S | 305.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-14 | 3.91 | 7.3 | 8.8 | 10 | 5 | N/S | 8 | 7 | 948 | 234 | 2 | <0.3 | 10.11 | 1.49 | N/S | N/S | 261.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-15 | 4.1 | 7.3 | 9.5 | N/S | N/S | N/S | 10 | 8 | 978 | 140 | N/S | N/S | N/S | N/S | N/S | N/S | 265.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-16 | 4.05 | 7.4 | 9.2 | N/S | N/S | N/S | 11 | 8 | 950 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 265.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-17 | 3.89 | 7.4 | 8.7 | N/S | N/S | N/S | 7 | 4 | 834 | 114 | <4 | <0.3 | 8.61 | 1.09 | N/S | N/S | 246.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-18 | 3.75 | 7.4 | 9.4 | 11 | 5 | <5 | 12 | 10 | 956 | 156 | 2 | <0.3 | 11.95 | 1.67 | <0.005 | <5 | 259.52 | 0.6 | 700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-03-19 | 3.75 | 7.4 | 9 | 15 | 8 | N/S | 18 | 16 | 1024 | 92 | 2 | <0.3 | 13.92 | 1.87 | N/S | N/S | 285.69 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.009 | 0.11 | 0.04 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-03-20 | 3.39 | 7.3 | 8.7 | 21 | 8 | N/S | 20 | 17 | 1058 | 100 | 3 | <0.3 | 12.83 | 2.39 | N/S | N/S | 295.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-21 | 2.26 | 7.4 | 8.1 | 16 | 8 | N/S | 17 | 15 | 1244 | 252 | <4 | <0.3 | 13.46 | 1.31 | N/S | N/S | 329.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-22 | 2.25 | 7.4 | 9 | N/S | N/S | N/S | 12 | 10 | 1038 | 134 | N/S | N/S | N/S | N/S | N/S | N/S | 290.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-23 | 2.98 | 7.5 | 8.3 | N/S | N/S | N/S | 6 | 5 | 1006 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 273.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-24 | 2.05 | 7.4 | 8.7 | N/S | N/S | N/S | 7 | 6 | 984 | 144 | <4 | <0.3 | 15.66 | 2.33 | N/S | N/S | 250.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-25 | 2.3 | 7.4 | 8.2 | 11 | 5 | <5 | 8 | 7 | 1000 | 166 | T/X | <0.3 | 16.06 | 2.35 | <0.005 | <5 | 224.33 | 0.8 | 2700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-03-26 | 3.54 | 7.4 | 7.9 | 26 | 10 | N/S | 30 | 26 | 976 | 154 | T/X | <0.3 | 12.29 | 1.84 | N/S | N/S | 277.46 | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.011 | 0.19 | 0.03 | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | T/X | N/S
2024-03-27 | 3.16 | 7.3 | 8.8 | 16 | 7 | N/S | 20 | 16 | 1050 | 190 | T/X | <0.3 | 11.57 | 1.87 | N/S | N/S | 296.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-28 | 2.79 | 7.3 | 8.6 | 15 | 6 | N/S | 14 | 12 | 1216 | 276 | T/X | <0.3 | 13.65 | 2 | N/S | N/S | 310.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-29 | 2.67 | 7.4 | 9.1 | N/S | N/S | N/S | 11 | 10 | 1136 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | 321.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-30 | 3.88 | 7.3 | 8.7 | N/S | N/S | N/S | 14 | 12 | 786 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 212.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-03-31 | 4.1 | 7.3 | 8.7 | N/S | N/S | N/S | 13 | 11 | 852 | 162 | T/X | <0.3 | 10.46 | 1.4 | N/S | N/S | 234.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-01 | 4.1 | 7.2 | 7.7 | 10 | 5 | <5 | 11 | 8 | 746 | 112 | T/X | <0.3 | 8.76 | 1.18 | <0.005 | <5 | 194.48 | 0.5 | 6800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-04-02 | 4.1 | 7.3 | 9.4 | 8 | 4 | N/S | 9 | 7 | 636 | 104 | T/X | <0.3 | 7.37 | 0.76 | N/S | N/S | 158.83 | N/S | N/S | <0.002 | 0.028 | <0.002 | <0.004 | 0.005 | 0.1 | 0.04 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 6.3 | N/S
2024-04-03 | 4.1 | 7.4 | 9.5 | T/X | T/X | N/S | 8 | 6 | 738 | 160 | T/X | <0.3 | 8.02 | 0.93 | N/S | N/S | 192.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-04 | 4.1 | 7.4 | 9.2 | T/X | T/X | N/S | 8 | 6 | 782 | 174 | T/X | <0.3 | 7.84 | 0.93 | N/S | N/S | 204.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-05 | 4.1 | 7.4 | 9.6 | N/S | N/S | N/S | 8 | 6 | 792 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | 198.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-06 | 3.97 | 7.5 | 9.5 | N/S | N/S | N/S | 7 | 6 | 856 | 134 | N/S | N/S | N/S | N/S | N/S | N/S | 216.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-07 | 3.91 | 7.4 | 9.4 | N/S | N/S | N/S | 9 | 7 | 926 | 138 | T/X | <0.3 | 12.24 | 1.4 | N/S | N/S | 249.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-08 | 4.1 | 7.4 | 8.7 | 7 | 3 | <5 | 7 | 6 | 886 | 174 | T/X | <0.3 | 9.71 | 1.22 | <0.005 | <5 | 225.33 | 0.5 | 1800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-04-09 | 4.1 | 7.4 | 9.2 | 7 | 4 | N/S | 8 | 6 | 916 | 140 | T/X | <0.3 | 11.52 | 1.3 | N/S | N/S | 246.96 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.007 | 0.12 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.9 | N/S
2024-04-10 | 4.05 | 7.4 | 9.3 | 6 | 4 | N/S | 6 | 5 | 894 | 124 | T/X | <0.3 | 12.63 | 1.48 | N/S | N/S | 231.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-11 | 4.02 | 7.4 | 8.9 | 7 | 4 | N/S | 6 | 5 | 924 | 158 | T/X | <0.3 | 13.27 | 1.51 | N/S | N/S | 241.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-12 | 3.94 | 7.4 | 9 | N/S | N/S | N/S | 7 | 6 | 950 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | 254.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-13 | 3.56 | 7.4 | 8.5 | N/S | N/S | N/S | 7 | 6 | 1106 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | 300.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-14 | 3.27 | 7.3 | 8.2 | N/S | N/S | N/S | 12 | 8 | 1064 | 108 | T/X | 3 | 7.53 | 2.83 | N/S | N/S | 317.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-15 | 2.1 | 7.4 | 8.1 | 9 | 4 | <5 | 7 | 5 | 1134 | 146 | T/X | 0.8 | 12.03 | 2.52 | <0.005 | <5 | 377.19 | 0.8 | 340000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-04-16 | 2.68 | 7.4 | 9 | 10 | 4 | N/S | 5 | 4 | 1116 | 112 | T/X | 1.2 | 14.55 | 2.25 | N/S | N/S | 341.73 | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.006 | 0.07 | 0.04 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2024-04-17 | 2.36 | 7.4 | 8.2 | 10 | 4 | N/S | 6 | 5 | 1182 | 174 | T/X | 1.1 | 13.07 | 2.44 | N/S | N/S | 351.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-18 | 2.06 | 7.4 | 8.9 | 7 | 4 | N/S | <4 | <4 | 1204 | 242 | T/X | <0.3 | T/X | 2.55 | N/S | N/S | 354.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-19 | 2.13 | 7.4 | 9.2 | N/S | N/S | N/S | <4 | <4 | 1172 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | 347.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-20 | 2.6 | 7.4 | 9.1 | N/S | N/S | N/S | 9 | 8 | 1084 | 134 | N/S | N/S | N/S | N/S | N/S | N/S | 314.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-21 | 2.12 | 7.4 | 8.6 | N/S | N/S | N/S | 13 | 12 | 1090 | 162 | T/X | 1.5 | 14.73 | 2.98 | N/S | N/S | 290.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-22 | 2.13 | 7.5 | 8.6 | 13 | 4 | <5 | 7 | 7 | 1052 | 104 | T/X | 1.3 | 14.57 | 3.06 | <0.005 | <5 | 297.92 | 0.9 | 2900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-04-23 | 2.38 | 7.5 | 8.8 | 10 | 4 | N/S | 5 | 5 | 1088 | 146 | T/X | 0.7 | 15.07 | 2.77 | N/S | N/S | 311.29 | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.006 | 0.07 | 0.05 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2024-04-24 | 1.99 | 7.4 | 8.9 | 5 | 3 | N/S | 5 | 4 | 1138 | 178 | T/X | <0.3 | 15.58 | 2.81 | N/S | N/S | 314.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-25 | 2.12 | 7.4 | 9 | 7 | 3 | N/S | 5 | 4 | 1168 | 180 | T/X | <0.3 | 17.66 | 3.01 | N/S | N/S | 284.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-26 | 2.57 | 7.4 | 8.8 | N/S | N/S | N/S | 5 | <4 | 1014 | 146 | N/S | N/S | N/S | N/S | N/S | N/S | 272.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-27 | 3.18 | 7.2 | 8 | N/S | N/S | N/S | 7 | 6 | 938 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 259.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-28 | 3.61 | 7.3 | 7.9 | N/S | N/S | N/S | 6 | 5 | 664 | 90 | T/X | <0.3 | 7.91 | 1.74 | N/S | N/S | 160.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-04-29 | 4.1 | 7.2 | 8.3 | 5 | 3 | <5 | 6 | 4 | 582 | 86 | T/X | <0.3 | 7.02 | 1.08 | <0.005 | <5 | 130.3 | 0.5 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-04-30 | 4.1 | 7.3 | 8.9 | 6 | 2 | N/S | 4 | <4 | 644 | 94 | T/X | <0.3 | 7.25 | 1 | N/S | N/S | 144.84 | N/S | N/S | <0.002 | 0.027 | <0.002 | <0.004 | 0.006 | 0.12 | 0.04 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 2.4 | N/S
2024-05-01 | 4.1 | 7.3 | 8.7 | 7 | 2 | N/S | 4 | <4 | 694 | 76 | T/X | 0.3 | 9.05 | 1.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-02 | 4.1 | 7.4 | 8.8 | 6 | 3 | N/S | 4 | <4 | 736 | 86 | T/X | T/X | 11.7 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-03 | 4.1 | 7.2 | 7.9 | N/S | N/S | N/S | 5 | <4 | 714 | 104 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-04 | 4.1 | 7.4 | 8.8 | N/S | N/S | N/S | <4 | <4 | 748 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-05 | 4.1 | 7.3 | 8.3 | N/S | N/S | N/S | <4 | <4 | 862 | 148 | T/X | <0.3 | 11.21 | 1.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-06 | 4.09 | 7.4 | 8.6 | 6 | <2 | <5 | <4 | <4 | 738 | 88 | T/X | <0.3 | 11.44 | 1.79 | <0.005 | <5 | 170.81 | 0.6 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-05-07 | 3.98 | 7.3 | 8.1 | 7 | 2 | N/S | 6 | 5 | 782 | 110 | T/X | <0.3 | 9.89 | 1.87 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.005 | 0.08 | 0.04 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-05-08 | 4.1 | 7.3 | 8.4 | 4 | <2 | N/S | <4 | 4 | 884 | 158 | T/X | <0.3 | 11.24 | 1.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-09 | 4.1 | 7.3 | 8.5 | 4 | <2 | N/S | <4 | <4 | 744 | 130 | T/X | <0.3 | 10.65 | 1.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-10 | 4.1 | 7.3 | 9.2 | N/S | N/S | N/S | 4 | <4 | 588 | 76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-11 | 4.1 | 7.4 | 9.1 | N/S | N/S | N/S | <4 | <4 | 686 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-12 | 4.09 | 7.4 | 9 | N/S | N/S | N/S | <4 | <4 | 796 | 114 | T/X | <0.3 | 10.71 | 1.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-13 | 4.02 | 7.3 | 8.3 | 4 | <2 | <5 | <4 | <4 | 854 | 138 | T/X | T/X | 11.1 | 1.59 | <0.005 | <5 | 217.34 | 0.6 | 910 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | N/S
2024-05-14 | 4.1 | 7.3 | 8.1 | 4 | <2 | N/S | <4 | <4 | 812 | 182 | T/X | 0.5 | 11.19 | 1.54 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.004 | 0.05 | 0.03 | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2024-05-15 | 4.1 | 7.4 | 9.1 | 4 | <2 | N/S | <4 | <4 | 748 | 140 | T/X | <0.3 | 10.74 | 1.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-16 | 4.1 | 7.4 | 9.3 | 4 | <2 | N/S | <4 | <4 | 772 | 98 | T/X | <0.3 | 13.26 | 1.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-17 | 4.1 | 7.4 | 8.2 | N/S | N/S | N/S | 7 | 6 | 842 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-18 | 3.91 | 7.2 | 7.7 | N/S | N/S | N/S | 7 | 6 | 912 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-19 | 2.44 | 7.3 | 8.1 | N/S | N/S | N/S | 9 | 7 | 996 | 218 | T/X | 0.3 | 8.85 | 1.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-20 | 2.54 | 7.3 | 7.4 | T/X | T/X | <5 | <4 | <4 | 860 | 88 | T/X | 0.5 | 11.53 | 2.41 | <0.005 | <5 | 228.61 | 0.8 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-05-21 | 2.43 | 7.4 | 8.6 | T/X | T/X | N/S | <4 | <4 | 888 | 126 | T/X | 1 | 16.37 | 1.95 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.003 | 0.05 | 0.04 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.5 | N/S
2024-05-22 | 2.32 | 7.4 | 7.9 | 2 | <2 | N/S | <4 | <4 | 856 | 104 | T/X | 0.4 | 12.09 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-23 | 2.05 | 7.5 | 8.6 | 4 | <2 | N/S | <4 | <4 | 888 | 158 | T/X | <0.3 | 17.72 | 2.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-24 | 2.83 | 7.5 | 9.1 | N/S | N/S | N/S | <4 | <4 | 858 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-25 | 2.26 | 7.3 | 8.6 | N/S | N/S | N/S | <4 | <4 | 836 | 114 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-26 | 3.1 | 7.4 | 8.9 | N/S | N/S | N/S | <4 | <4 | 770 | 142 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-27 | 3.85 | 7.2 | 8.3 | <2 | <2 | <5 | <4 | <4 | 714 | 136 | T/X | <0.3 | 12.29 | 1.68 | <0.005 | <5 | 148.76 | 0.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 6
2024-05-28 | 3.35 | 7.3 | 8.5 | <2 | <2 | N/S | <4 | <4 | 810 | 150 | T/X | <0.3 | 12.03 | 1.74 | N/S | N/S | N/S | N/S | 1400 | <0.002 | 0.03 | <0.002 | <0.004 | 0.003 | 0.04 | 0.03 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.016 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | <0.5 | N/S
2024-05-29 | 3.16 | 7.3 | 9.3 | 2 | <2 | N/S | <4 | <4 | 860 | 164 | T/X | <0.3 | 12.82 | 1.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-30 | 2.72 | 7.4 | 8.7 | 3 | <2 | N/S | <4 | <4 | 822 | 110 | T/X | <0.3 | 14.93 | 2.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-05-31 | 2.02 | 7.4 | 8.8 | N/S | N/S | N/S | <4 | <4 | 998 | 190 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-01 | 2.75 | 7.5 | 9 | N/S | N/S | N/S | <4 | <4 | 864 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-02 | 4 | 7.3 | 8.5 | N/S | N/S | N/S | <4 | <4 | 788 | 144 | T/X | <0.3 | 11.16 | 1.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-03 | 3.57 | 7.3 | 8.3 | 3 | <2 | <5 | <4 | <4 | 790 | 130 | T/X | <0.3 | 9.93 | 1.45 | <0.005 | <5 | 166.08 | 0.6 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 6
2024-06-04 | 2.97 | 7.3 | 8.7 | 4 | <2 | N/S | <4 | <4 | 922 | 142 | T/X | <0.3 | 11.92 | 1.9 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.004 | 0.07 | 0.04 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.02 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2024-06-05 | 3.65 | 7.3 | 8.4 | 7 | 3 | N/S | <4 | <4 | 734 | 82 | T/X | <0.3 | 8 | 1.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-06 | 4.01 | 7.3 | 7.9 | 6 | <2 | N/S | 4 | 4 | 844 | 148 | T/X | 0.6 | 8.62 | 1.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-07 | 3.72 | 7.4 | 8.3 | N/S | N/S | N/S | <4 | <4 | 874 | 86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-08 | 2.32 | 7.3 | 8.2 | N/S | N/S | N/S | <4 | <4 | 978 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-09 | 2.43 | 7.4 | 8.7 | N/S | N/S | N/S | 6 | <4 | 1006 | 136 | T/X | 0.7 | 16.96 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-10 | 2.36 | 7.4 | 7.9 | T/X | T/X | <5 | 4 | <4 | 1184 | 260 | T/X | 0.9 | 14.83 | 2.87 | <0.005 | <5 | 310.72 | 0.8 | 4500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-06-11 | 2.52 | 7.4 | 8.8 | T/X | T/X | N/S | 8 | 6 | 1004 | 138 | T/X | 0.7 | 14.89 | 2.68 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.007 | 0.1 | 0.04 | <0.002 | 0.016 | 0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.9 | N/S
2024-06-12 | 1.96 | 7.4 | 8.3 | T/X | T/X | N/S | 4 | <4 | 1134 | 246 | T/X | <0.3 | 12.82 | 2.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-13 | 1.96 | 7.4 | 8.4 | 4 | <2 | N/S | 6 | <4 | 1202 | 296 | T/X | <0.3 | 14.64 | 2.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-14 | 2.61 | 7.3 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1152 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-15 | 2.13 | 7.5 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1170 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-16 | 2.1 | 7.5 | 8.3 | N/S | N/S | N/S | 4 | <4 | 1170 | 204 | T/X | <0.3 | 16.2 | 2.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-17 | 2.08 | 7.4 | 8.1 | T/X | T/X | <5 | <4 | 5 | 1008 | 184 | T/X | <0.3 | 16.95 | 2.91 | <0.005 | <5 | 275.51 | 0.9 | 4100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-06-18 | 2.07 | 7.5 | 8.2 | T/X | T/X | N/S | <4 | <4 | 1044 | 150 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.005 | 0.06 | 0.04 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-06-19 | 2.09 | 7.3 | 8.4 | T/X | T/X | N/S | <4 | <4 | 1044 | 136 | T/X | <0.3 | 20.35 | 3.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-20 | 2.9 | 7.4 | 8.7 | T/X | T/X | N/S | <4 | <4 | 1136 | 250 | T/X | <0.3 | 21.53 | 3.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-21 | 2.12 | 7.4 | 8.9 | N/S | N/S | N/S | 4 | 4 | 1070 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-22 | 2.11 | 7.4 | 8.7 | N/S | N/S | N/S | 4 | 4 | 1104 | 170 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-23 | 3.88 | 7.2 | 8.3 | N/S | N/S | N/S | 5 | 4 | 934 | 162 | T/X | <0.3 | 12.42 | 2.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-24 | 3.12 | 7.2 | 8.1 | 4 | <2 | <5 | 4 | <4 | 912 | 122 | T/X | <0.3 | 9.77 | 1.95 | <0.005 | <5 | 263.48 | 0.7 | 6800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 6
2024-06-25 | 3.09 | 7.5 | 8.6 | T/X | T/X | N/S | 4 | <4 | 1074 | 164 | T/X | <0.3 | 10.85 | 2.16 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.003 | 0.05 | 0.02 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-06-26 | 3.51 | 7.2 | 8.3 | 9 | 2 | N/S | <4 | <4 | 1074 | 158 | T/X | <0.3 | 9.54 | 1.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-27 | 2.11 | 7.3 | 8.6 | T/X | T/X | N/S | 5 | 4 | 1192 | 112 | T/X | <0.3 | 11.08 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-28 | 2.44 | 7.5 | 8.4 | N/S | N/S | N/S | 8 | 5 | 1312 | 224 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-29 | 2.32 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1268 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-06-30 | 2.19 | 7.5 | 8 | N/S | N/S | N/S | 5 | 4 | 1364 | 186 | T/X | 0.4 | 10.28 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-01 | 2.17 | 7.5 | 8.6 | 4 | <2 | <5 | 4 | <4 | 1450 | 284 | T/X | <0.3 | 15.19 | 2.92 | <0.005 | T/X | 443.13 | 0.9 | 5300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-07-02 | 2.19 | 7.4 | 7.9 | 5 | <2 | N/S | 4 | <4 | 1512 | 316 | T/X | 0.3 | 13.49 | 2.77 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.003 | 0.05 | 0.04 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-07-03 | 2.02 | 7.5 | 8.3 | T/X | T/X | N/S | 5 | 4 | 1502 | 284 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-04 | 2.07 | 7.6 | 8.3 | 5 | 2 | N/S | 5 | 4 | 1370 | 194 | T/X | <0.3 | 19.86 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-05 | 2.06 | 7.5 | 8.4 | N/S | N/S | N/S | 9 | 6 | 1512 | 338 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-06 | 2.06 | 7.4 | 8.6 | N/S | N/S | N/S | 7 | 6 | 1468 | 348 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-07 | 2.4 | 7.4 | 8.7 | N/S | N/S | N/S | 7 | 6 | 1278 | 314 | T/X | <0.3 | 20.41 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-08 | 2.76 | 7.3 | 7.9 | 6 | 2 | <5 | 5 | <4 | 1450 | 330 | T/X | <0.3 | 14.97 | 2.66 | <0.005 | T/X | 306.85 | 0.8 | 25000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-07-09 | 2.32 | 7.5 | 8.2 | 5 | 2 | N/S | <4 | <4 | 1096 | 180 | T/X | <0.3 | 17.05 | 2.65 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.004 | 0.05 | 0.03 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.9 | N/S
2024-07-10 | 3.78 | 7.3 | 8 | 7 | 5 | N/S | <4 | <4 | 912 | 164 | T/X | <0.3 | 11.03 | 1.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-11 | 3.41 | 7.3 | 8 | 5 | 3 | N/S | <4 | <4 | 892 | 124 | T/X | <0.3 | 11.09 | 1.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-12 | 1.98 | 7.5 | 8.4 | N/S | N/S | N/S | 5 | <4 | 862 | 124 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-13 | 2.02 | 7.4 | 8.7 | N/S | N/S | N/S | 4 | <4 | 966 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-14 | 2.64 | 7.4 | 8.4 | N/S | N/S | N/S | 4 | <4 | 1042 | 136 | T/X | 0.7 | 14.65 | 2.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-15 | 4 | 7.3 | 7.7 | 5 | 3 | <5 | 5 | <4 | 764 | 98 | T/X | <0.3 | 7.61 | 1.75 | <0.005 | <5 | 190.06 | 0.6 | 59000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-07-16 | 4.1 | 7.2 | 7.9 | 5 | 3 | N/S | 4 | <4 | 756 | 118 | T/X | <0.3 | 6.76 | 1.37 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.003 | 0.04 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-07-17 | 4.02 | 7.4 | 8.1 | 4 | 3 | N/S | <4 | <4 | 926 | 184 | T/X | <0.3 | 8.5 | 1.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-18 | 3.6 | 7.3 | 8.2 | 5 | 3 | N/S | 6 | 5 | 1116 | 254 | T/X | <0.3 | 9.61 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-19 | 2.06 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1180 | 276 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-20 | 2.02 | 7.5 | 8.7 | N/S | N/S | N/S | <4 | <4 | 1210 | 220 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-21 | 2.02 | 7.5 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1130 | 224 | T/X | <0.3 | 17.71 | 3.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-22 | 2.02 | 7.3 | 8.4 | 5 | 3 | <5 | <4 | <4 | 1252 | 324 | T/X | <0.3 | 17.71 | 3.09 | <0.005 | <5 | 316.59 | 0.9 | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-07-23 | 2.72 | 7.5 | 8.6 | 6 | 3 | N/S | <4 | 4 | 1188 | 180 | T/X | 3.2 | 14.01 | 2.81 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.004 | 0.06 | 0.04 | <0.002 | 0.019 | <0.002 | <0.004 | <0.004 | 0.025 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2024-07-24 | 2.02 | 7.4 | 8 | 4 | 3 | N/S | <4 | <4 | 1192 | 196 | T/X | 0.7 | 13.23 | 2.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-25 | 2.03 | 7.5 | 8.5 | 4 | 3 | N/S | <4 | <4 | 1256 | 208 | T/X | <0.3 | 16.6 | 2.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-26 | 2.05 | 7.5 | 8.7 | N/S | N/S | N/S | <4 | <4 | 1342 | 240 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-27 | 2.07 | 7.4 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1402 | 224 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-28 | 2.07 | 7.4 | 8.6 | N/S | N/S | N/S | 5 | <4 | 1398 | 246 | T/X | <0.3 | 19.79 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-07-29 | 2.07 | 7.5 | 8.4 | 3 | <2 | <5 | 4 | <4 | 1282 | 176 | T/X | <0.3 | 17.05 | 3.1 | <0.005 | <5 | 387.02 | 0.9 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-07-30 | 2.07 | 7.5 | 8.5 | 3 | <2 | N/S | <4 | <4 | 1296 | 238 | T/X | <0.3 | 18.26 | 3.05 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.004 | 0.04 | 0.04 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2024-07-31 | 2.07 | 7.5 | 8.4 | 3 | <2 | N/S | <4 | <4 | 1412 | 274 | T/X | <0.3 | 19.3 | 3.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-01 | 2.08 | 7.5 | 8.3 | 3 | <2 | N/S | <4 | <4 | 1448 | 300 | T/X | <0.3 | 18.81 | 3.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-02 | 2.08 | 7.4 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1700 | 526 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-03 | 2.08 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1502 | 304 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-04 | 2.07 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1380 | 218 | T/X | <0.3 | 18.89 | 3.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-05 | 3.02 | 7.4 | 8.2 | 5 | <2 | <5 | <4 | <4 | 1190 | 214 | T/X | 0.3 | 13.47 | 2.92 | <0.005 | <5 | 353.85 | 0.8 | 800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-08-06 | 1.9 | 7.4 | 7.9 | 4 | <2 | N/S | <4 | <4 | 1284 | 354 | T/X | <0.3 | 11.6 | 2.63 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.003 | 0.05 | 0.03 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2024-08-07 | 1.99 | 7.5 | 8.2 | 4 | <2 | N/S | <4 | <4 | 1264 | 256 | T/X | <0.3 | 15.13 | 2.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-08 | 1.96 | 7.4 | 8.2 | 6 | 3 | N/S | 11 | 10 | 1212 | 218 | T/X | <0.3 | 7.41 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-09 | 2.04 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1310 | 230 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-10 | 2.04 | 7.4 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1352 | 256 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-11 | 2 | 7.4 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1320 | 276 | T/X | <0.3 | 19.75 | 3.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-12 | 2.02 | 7.4 | 8.4 | 5 | 2 | <5 | <4 | <4 | 1252 | 268 | T/X | <0.3 | 20.53 | 3.83 | <0.005 | <5 | 297.68 | 1 | 9800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-08-13 | 1.94 | 7.5 | 8.5 | 6 | 2 | N/S | <4 | <4 | 1174 | 258 | T/X | <0.3 | 20.14 | 3.52 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.003 | 0.04 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-08-14 | 1.96 | 7.5 | 8.3 | 5 | <2 | N/S | <4 | 4 | 1116 | 112 | T/X | <0.3 | 18.94 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-15 | 2.07 | 7.5 | 8.2 | 5 | <2 | N/S | <4 | <4 | 1112 | 192 | T/X | <0.3 | 18.27 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-16 | 3.61 | 7.3 | 7.9 | N/S | N/S | N/S | <4 | <4 | 928 | 126 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-17 | 2.32 | 7.3 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1042 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-18 | 2.21 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1054 | 130 | T/X | <0.3 | 14.46 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-19 | 2.62 | 7.5 | 8.4 | 8 | 3 | <5 | 4 | <4 | 1228 | 256 | T/X | 0.9 | 12.37 | 4.07 | <0.005 | <5 | 320.62 | 0.8 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-08-20 | 2.41 | 7.4 | 8.5 | 6 | 2 | N/S | <4 | <4 | 1340 | 314 | T/X | 0.7 | 14.12 | 2.72 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.004 | 0.07 | 0.03 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-08-21 | 1.33 | 7.4 | 7.9 | 5 | <2 | N/S | <4 | <4 | 1330 | 270 | T/X | 0.3 | 13.96 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-22 | 2.31 | 7.5 | 8.3 | 5 | <2 | N/S | <4 | <4 | 1310 | 210 | T/X | <0.3 | 17.29 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-23 | 2.04 | 7.5 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1652 | 422 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-24 | 2.04 | 7.5 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1514 | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-25 | 2.03 | 7.5 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1514 | 356 | T/X | <0.3 | 18.14 | 3.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-26 | 2.03 | 7.5 | 8.1 | 6 | <2 | <5 | 6 | 5 | 1392 | 264 | T/X | <0.3 | 17.2 | 3.47 | <0.005 | <5 | 425.93 | 1 | 34000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-08-27 | 2.07 | 7.5 | 8.1 | 5 | <2 | N/S | <4 | <4 | 1364 | 302 | T/X | <0.3 | 16.44 | 3.76 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.004 | 0.06 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-08-28 | 3.88 | 7.3 | 8.2 | 4 | <2 | N/S | <4 | <4 | 1124 | 346 | T/X | <0.3 | 10.64 | 0.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-29 | 3.68 | 7.3 | 8.2 | 4 | 2 | N/S | <4 | <4 | 910 | 140 | T/X | <0.3 | 10.81 | 1.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-30 | 2.14 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 1200 | 276 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-08-31 | 2.01 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1188 | 254 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-01 | 2 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1342 | 294 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-02 | 1.98 | 7.4 | 8.3 | 3 | <2 | <5 | <4 | <4 | 1426 | 276 | T/X | <0.3 | 21 | 3.31 | <0.005 | <5 | 417.48 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 7
2024-09-03 | 1.99 | 7.4 | 8.3 | 4 | <2 | N/S | <4 | <4 | 1432 | 298 | T/X | <0.3 | 20.99 | 3.33 | N/S | N/S | N/S | N/S | 1200 | <0.002 | 0.041 | <0.002 | <0.004 | 0.006 | 0.05 | 0.03 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | T/X | N/S
2024-09-04 | 1.98 | 7.5 | 8.4 | 4 | <2 | N/S | <4 | <4 | 1328 | 174 | T/X | 0.4 | 22.91 | 3.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-09-05 | 1.97 | 7.5 | 8.4 | 4 | <2 | N/S | <4 | 4 | 1322 | 186 | T/X | <0.3 | 20.91 | 3.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-06 | 1.87 | 7.5 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1298 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-07 | 2.05 | 7.4 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1300 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-08 | 1.84 | 7.5 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1256 | 222 | T/X | <0.3 | 20.93 | 3.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-09 | 1.96 | 7.5 | 8.2 | 3 | <2 | <5 | <4 | <4 | 1238 | 220 | T/X | <0.3 | 20.2 | 3.05 | <0.005 | <5 | 326.42 | 1 | 1100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-09-10 | 1.96 | 7.4 | 8.2 | 5 | <2 | N/S | <4 | <4 | 1258 | 306 | T/X | <0.3 | 18.77 | 3.18 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.004 | 0.05 | 0.03 | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2024-09-11 | 1.84 | 7.5 | 8 | 4 | <2 | N/S | <4 | <4 | 1156 | 194 | T/X | 0.4 | 17.75 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-12 | 1.93 | 7.5 | 8 | 8 | <2 | N/S | <4 | <4 | 1160 | 214 | T/X | <0.3 | 13.45 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-13 | 1.98 | 7.5 | 7.9 | N/S | N/S | N/S | 4 | <4 | 1094 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-14 | 1.94 | 7.4 | 7.7 | N/S | N/S | N/S | 5 | 4 | 1140 | 190 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-15 | 1.92 | 7.4 | 7.9 | N/S | N/S | N/S | 6 | 5 | 1112 | 194 | T/X | <0.3 | 17 | 3.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-16 | 1.95 | 7.4 | 7.8 | 9 | 3 | <5 | 5 | 4 | 1166 | 266 | T/X | <0.3 | 17.98 | 3.48 | <0.005 | 6 | 291.64 | 1 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-09-17 | 1.85 | 7.5 | 8.2 | 9 | 3 | N/S | <4 | <4 | 1150 | 238 | T/X | 1 | 20.41 | 3.41 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.09 | 0.03 | <0.002 | 0.045 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-09-18 | 1.85 | 7.4 | 7.7 | 5 | <2 | N/S | 4 | 4 | 1176 | 262 | T/X | <0.3 | 22.67 | 3.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-19 | 1.84 | 7.6 | 7.9 | 7 | 3 | N/S | 5 | 4 | 1170 | 222 | T/X | <0.3 | 22.04 | 3.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-20 | 1.82 | 7.5 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1254 | 234 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-21 | 1.82 | 7.5 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1326 | 274 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-22 | 2.69 | 7.5 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1284 | 314 | T/X | <0.3 | 18.07 | 2.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-23 | 3.58 | 7.2 | 7.8 | <2 | <2 | <5 | <4 | <4 | 1026 | 142 | T/X | <0.3 | 10.94 | 1.9 | <0.005 | <5 | 316.13 | 0.7 | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-09-24 | 2.13 | 7.5 | 8 | <2 | <2 | N/S | <4 | <4 | 984 | 176 | T/X | <0.3 | 11.91 | 1.99 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.029 | <0.002 | <0.004 | 0.002 | 0.03 | 0.02 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2024-09-25 | 4.1 | 7.2 | 7.9 | 3 | <2 | N/S | <4 | <4 | 886 | 116 | T/X | <0.3 | 9.25 | 1.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-26 | 2.37 | 7.4 | 8 | 3 | <2 | N/S | <4 | 4 | 1082 | 126 | T/X | <0.3 | 12.11 | 2.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-27 | 2.12 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1206 | 182 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-28 | 2.22 | 7.5 | 8.1 | N/S | N/S | N/S | 9 | 7 | 1208 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-29 | 2.12 | 7.5 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1232 | 212 | T/X | <0.3 | 14.78 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-09-30 | 2.05 | 7.4 | 8.2 | 3 | <2 | <5 | <4 | <4 | 1138 | 114 | T/X | <0.3 | 18.07 | 2.98 | <0.005 | <5 | 353.7 | 1 | 2700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-10-01 | 2 | 7.5 | 8.3 | 3 | <2 | N/S | <4 | <4 | 1220 | 176 | T/X | <0.3 | 18.97 | 3.1 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.003 | 0.05 | 0.03 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-10-02 | 1.93 | 7.5 | 8.8 | <2 | <2 | N/S | <4 | <4 | 1232 | 210 | T/X | <0.3 | 20.71 | 2.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-03 | 1.98 | 7.5 | 8.3 | 4 | 2 | N/S | <4 | <4 | 1328 | 272 | T/X | <0.3 | 19.41 | 3.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-04 | 2.25 | 7.5 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1160 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-05 | 2.06 | 7.6 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1058 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-06 | 2.03 | 7.6 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1068 | 134 | T/X | <0.3 | 19.86 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-07 | 1.88 | 7.5 | 8.4 | 2 | <2 | <5 | <4 | <4 | 1126 | 138 | T/X | <0.3 | 21.45 | 3.07 | <0.005 | <5 | 321.82 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 6
2024-10-08 | 1.88 | 7.5 | 8.6 | 3 | <2 | N/S | <4 | <4 | 1142 | 132 | T/X | <0.3 | 23.9 | 3.2 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.003 | 0.04 | 0.03 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-10-09 | 1.85 | 7.5 | 8.3 | 2 | <2 | N/S | <4 | <4 | 1116 | 112 | T/X | 0.4 | 21.78 | 3.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-10 | 1.88 | 7.5 | 8.4 | 4 | <2 | N/S | <4 | <4 | 1214 | 174 | T/X | <0.3 | 25.03 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-11 | 1.88 | 7.5 | 8.3 | N/S | N/S | N/S | 7 | 7 | 1352 | 152 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-12 | 1.89 | 7.5 | 8.2 | N/S | N/S | N/S | 6 | 5 | 1432 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-13 | 1.88 | 7.5 | 8.1 | N/S | N/S | N/S | 7 | 6 | 1404 | 160 | T/X | <0.3 | 19.88 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-14 | 1.88 | 7.3 | 8.4 | 7 | <2 | <5 | 9 | 7 | 1400 | 160 | T/X | <0.3 | 19.15 | 3.64 | <0.005 | <5 | 470.47 | 1 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-10-15 | 1.95 | 7.5 | 9 | 7 | 3 | N/S | 4 | 4 | 1348 | 138 | T/X | <0.3 | 18.85 | 3.19 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.007 | 0.06 | 0.03 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2024-10-16 | 1.89 | 7.4 | 8.3 | 3 | <2 | N/S | <4 | <4 | 1296 | 134 | T/X | <0.3 | 21.18 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-17 | 1.85 | 7.5 | 8.6 | 4 | <2 | N/S | <4 | <4 | 1330 | 168 | T/X | <0.3 | 22.85 | 3.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-18 | 1.86 | 7.5 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1334 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-19 | 1.91 | 7.6 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1340 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-20 | 1.96 | 7.4 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1298 | 174 | T/X | <0.3 | 21.55 | 3.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-21 | 1.84 | 7.5 | 8 | 2 | <2 | <5 | <4 | <4 | 1294 | 176 | T/X | <0.3 | 22.44 | 3.09 | <0.005 | <5 | 373.54 | 1.1 | 1100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-10-22 | 1.81 | 7.6 | 8 | <2 | <2 | N/S | 4 | <4 | 1296 | 164 | T/X | <0.3 | 23.22 | 3.28 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.004 | 0.03 | 0.03 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-10-23 | 1.82 | 7.3 | 8.8 | 5 | <2 | N/S | 4 | <4 | 1246 | 168 | T/X | <0.3 | 23.81 | 3.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-24 | 1.8 | 7.5 | 8.5 | 7 | 3 | N/S | <4 | 4 | 1256 | 138 | T/X | <0.3 | 23.45 | 3.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-25 | 2.97 | 7.3 | 8.2 | N/S | N/S | N/S | <4 | <4 | 968 | 182 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-26 | 2.25 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1010 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-27 | 2.02 | 7.5 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1082 | 272 | T/X | <0.3 | 19.89 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-28 | 1.82 | 7.3 | 8.4 | 7 | 2 | <5 | 6 | 4 | 1122 | 136 | T/X | <0.3 | 21.33 | 3.48 | <0.005 | <5 | 302.41 | 1 | 17000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-10-29 | 1.89 | 7.4 | 8.2 | 7 | 2 | N/S | 6 | 4 | 1176 | 142 | T/X | <0.3 | 19.84 | 3.53 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.031 | <0.002 | <0.004 | 0.006 | 0.06 | 0.03 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-10-30 | 2 | 7.4 | 8.2 | 7 | <2 | N/S | 4 | <4 | 1180 | 198 | T/X | <0.3 | 19.48 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-10-31 | 1.88 | 7.4 | 7.9 | 7 | <2 | N/S | 5 | 5 | 1414 | 248 | T/X | <0.3 | 22.98 | 3.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-01 | 1.8 | 7.4 | 9.1 | N/S | N/S | N/S | <4 | <4 | 1408 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-02 | 1.78 | 7.5 | 7.9 | N/S | N/S | N/S | 4 | 5 | 1556 | 238 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-03 | 1.93 | 7.6 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1448 | 202 | T/X | <0.3 | 23.06 | 3.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-04 | 2 | 7.4 | 8.7 | 7 | <2 | <5 | 5 | 4 | 1262 | 126 | T/X | <0.3 | 19.9 | 3.1 | <0.005 | <5 | 387.71 | 1 | 3500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2024-11-05 | 3.4 | 7.4 | 8.4 | 7 | 2 | N/S | 7 | 8 | 912 | 202 | T/X | 0.4 | 12.25 | 2.15 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.028 | <0.002 | <0.004 | 0.005 | 0.07 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.016 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-11-06 | 3.72 | 7.2 | 8.2 | 7 | 2 | N/S | <4 | <4 | 862 | 166 | T/X | <0.3 | 12.5 | 1.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-07 | 3.33 | 7.2 | 7.9 | 5 | <2 | N/S | 6 | 4 | 952 | 124 | T/X | <0.3 | 14.24 | 1.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-08 | 2.92 | 7.3 | 8.3 | N/S | N/S | N/S | 5 | 5 | 1244 | 318 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-09 | 2.18 | 7.4 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1356 | 396 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-10 | 2.88 | 7.3 | 8 | N/S | N/S | N/S | <4 | <4 | 1052 | 220 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-11 | 2.3 | 7.4 | 8.2 | 3 | <2 | <5 | <4 | <4 | 1042 | 206 | T/X | <0.3 | 16.69 | 2.6 | <0.005 | <5 | 278.05 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 6
2024-11-12 | 2.05 | 7.4 | 8.8 | 4 | <2 | N/S | <4 | <4 | 1076 | 148 | T/X | <0.3 | 20.1 | 2.92 | N/S | N/S | N/S | N/S | 9500 | <0.002 | 0.031 | <0.002 | <0.004 | 0.006 | 0.06 | 0.03 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | <0.5 | N/S
2024-11-13 | 2.06 | 7.5 | 8.8 | <2 | <2 | N/S | 5 | <4 | 1100 | 306 | T/X | <0.3 | 19.59 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-14 | 3.41 | 7.3 | 8.7 | <2 | <2 | N/S | 5 | 4 | 804 | 88 | T/X | <0.3 | 14.08 | 2.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-15 | 2.74 | 7.4 | 8.7 | N/S | N/S | N/S | 5 | 4 | 934 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-16 | 2.29 | 7.5 | 8.6 | N/S | N/S | N/S | 6 | <4 | 952 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-17 | 2.21 | 7.5 | 8.3 | N/S | N/S | N/S | 5 | 5 | 1094 | 326 | T/X | <0.3 | 17.74 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-18 | 1.91 | 7.4 | 8.3 | 3 | <2 | <5 | 6 | 5 | 728 | 130 | T/X | <0.3 | 18.22 | 2.5 | N/S | <5 | 219.87 | 0.9 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 7
2024-11-19 | 2.49 | 7.4 | 8.9 | <2 | <2 | N/S | <4 | <4 | 470 | 130 | T/X | <0.3 | 12.7 | 1.96 | <0.005 | N/S | N/S | N/S | N/S | <0.002 | 0.022 | <0.002 | <0.004 | 0.004 | 0.04 | 0.02 | <0.002 | 0.002 | <0.002 | <0.004 | <0.004 | 0.017 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 0.6 | N/S
2024-11-20 | 2.75 | 7.4 | 9.1 | <2 | <2 | N/S | <4 | <4 | 706 | 106 | T/X | <0.3 | 14.01 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-21 | 3.15 | 7.4 | 8.9 | 2 | <2 | N/S | 10 | 6 | 918 | 130 | T/X | <0.3 | 14.99 | 1.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-22 | 3.17 | 7.5 | 9.5 | N/S | N/S | N/S | 4 | 5 | 666 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-23 | 3.12 | 7.3 | 8.7 | N/S | N/S | N/S | <4 | <4 | 930 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-24 | 3.02 | 7.3 | 8.5 | N/S | N/S | N/S | 4 | 4 | 906 | 132 | T/X | <0.3 | 16.62 | 2.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-25 | 2.78 | 7.2 | 8 | 4 | <2 | <5 | 5 | <4 | 1066 | 256 | T/X | <0.3 | 15.54 | 2.65 | <0.005 | <5 | 266.81 | 0.8 | 1600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-11-26 | 2.19 | 7.5 | 8.6 | <2 | <2 | N/S | <4 | <4 | 958 | 136 | T/X | <0.3 | 17.13 | 2.72 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.03 | <0.002 | <0.004 | 0.003 | 0.03 | 0.03 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-11-27 | 2.02 | 7.4 | 8.8 | 7 | <2 | N/S | 4 | 4 | 1158 | 240 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-28 | 2.31 | 7.5 | 8.3 | <2 | <2 | N/S | <4 | <4 | 780 | 84 | T/X | <0.3 | 18.34 | 2.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-29 | 2.03 | 7.4 | 9.5 | N/S | N/S | N/S | <4 | <4 | 1008 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-11-30 | 2.11 | 7.4 | 9 | N/S | N/S | N/S | <4 | <4 | 966 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-01 | 2.11 | 7.3 | 9.1 | N/S | N/S | N/S | <4 | <4 | 954 | 132 | T/X | <0.3 | 22.25 | 2.88 | N/S | N/S | 232.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-02 | 1.99 | 7.4 | 9 | <2 | <2 | <5 | 4 | <4 | 886 | 104 | T/X | <0.3 | 21.78 | 2.94 | <0.005 | 24 | 249.94 | 1 | 3100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-12-03 | 1.98 | 7.4 | 10.2 | <2 | <2 | N/S | 4 | <4 | 982 | 136 | T/X | <0.3 | 22.47 | 2.92 | N/S | N/S | 298.1 | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.004 | 0.04 | 0.02 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-12-04 | 1.95 | 7.4 | 9.1 | <2 | <2 | N/S | <4 | <4 | 1036 | 122 | T/X | <0.3 | 23.84 | 2.9 | N/S | N/S | 282.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-05 | 1.98 | 7.4 | 9.5 | 2 | <2 | N/S | <4 | <4 | 1010 | 124 | T/X | <0.3 | 24.54 | 2.99 | N/S | N/S | 272.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-06 | 2 | 7.4 | 9.6 | N/S | N/S | N/S | 5 | <4 | 966 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | 239.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-07 | 2.08 | 7.4 | 9 | N/S | N/S | N/S | 5 | 4 | 1000 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 242.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-08 | 2.09 | 7.4 | 8.5 | N/S | N/S | N/S | 4 | <4 | 976 | 110 | T/X | 1 | 22.62 | 3.28 | N/S | N/S | 252.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-09 | 1.96 | 7.3 | 8.3 | 4 | <2 | <5 | <4 | <4 | 878 | 106 | T/X | 0.4 | 21.77 | 3.18 | <0.005 | <5 | 252.63 | 1 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2024-12-10 | 1.96 | 7.4 | 8.7 | 4 | <2 | N/S | <4 | <4 | 764 | 84 | T/X | <0.3 | 22.5 | 3.28 | N/S | N/S | 232.54 | N/S | N/S | <0.002 | 0.029 | <0.002 | <0.004 | 0.005 | 0.05 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2024-12-11 | 1.83 | 7.4 | 9.1 | 10 | 2 | N/S | 5 | 4 | 914 | 112 | T/X | 0.6 | 21.68 | 3.49 | N/S | N/S | 236.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-12 | 1.98 | 7.4 | 9.2 | 5 | <2 | N/S | 5 | 6 | 1276 | 414 | T/X | <0.3 | 22.92 | 3.21 | N/S | N/S | 228.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-13 | 7.97 | 7.4 | 9.6 | N/S | N/S | N/S | 8 | 5 | 724 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | 260.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-14 | 2.19 | 7.3 | 9.3 | N/S | N/S | N/S | <4 | <4 | 1000 | 198 | N/S | N/S | N/S | N/S | N/S | N/S | 220.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-15 | 2.89 | 7.2 | 8.8 | N/S | N/S | N/S | 6 | 5 | 896 | 170 | T/X | <0.3 | 17 | 2.73 | N/S | N/S | 213.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-16 | 2.84 | 7.2 | 8.5 | 9 | 3 | <5 | 7 | 5 | 828 | 128 | T/X | 0.7 | 14.78 | 2.57 | <0.005 | <5 | 258.05 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2024-12-17 | 2.28 | 7.4 | 7.9 | 3 | <2 | N/S | 4 | <4 | 1088 | 216 | T/X | 0.4 | 17 | 2.68 | N/S | N/S | 331.45 | N/S | 9300 | <0.002 | 0.035 | <0.002 | <0.004 | 0.004 | 0.04 | 0.03 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2024-12-18 | 2.17 | 7.4 | 7.9 | 7 | 3 | N/S | 7 | 5 | 1226 | 336 | T/X | 0.4 | 20.29 | 2.99 | N/S | N/S | 330.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-19 | 2.12 | 7.4 | 8.2 | 3 | <2 | N/S | 7 | 7 | 1042 | 290 | T/X | 0.5 | 21.79 | 3.05 | N/S | N/S | 347.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-20 | 2.41 | 7.3 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1514 | 340 | N/S | N/S | N/S | N/S | N/S | N/S | 468.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-21 | 2.38 | 7.3 | 8.2 | N/S | N/S | N/S | 7 | 6 | 1478 | 210 | N/S | N/S | N/S | N/S | N/S | N/S | 496.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-22 | 2.27 | 7.4 | 8 | N/S | N/S | N/S | 7 | 7 | 1270 | 182 | T/X | 2.5 | 16.53 | 2.88 | N/S | N/S | 414.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-23 | 2.24 | 7.4 | 7.8 | 20 | 5 | <5 | 8 | 7 | 1226 | 126 | T/X | 2.5 | 14.04 | 2.83 | <0.005 | <5 | 385.75 | 1 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 14
2024-12-24 | 2.27 | 7.4 | 8 | T/X | T/X | N/S | 5 | 5 | 1216 | 134 | T/X | T/X | T/X | T/X | N/S | N/S | 403.75 | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.05 | N/S | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2024-12-25 | 2.1 | 7.6 | 7.9 | 9 | 3 | N/S | 5 | 5 | 1222 | 192 | T/X | 4.3 | 13.36 | 2.95 | N/S | N/S | 376.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 0.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-26 | 2.12 | 7.5 | 7.7 | 24 | 7 | N/S | 14 | 13 | 1116 | 158 | T/X | 4.2 | 14.94 | 3.37 | N/S | N/S | 392.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-27 | 2.29 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 4 | 1450 | 376 | N/S | N/S | N/S | N/S | N/S | N/S | 409.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-28 | 2.82 | 7.4 | 7.1 | N/S | N/S | N/S | <4 | <4 | 1104 | 104 | N/S | N/S | N/S | N/S | N/S | N/S | 411.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-29 | 3.24 | 7.4 | 7.6 | N/S | N/S | N/S | 5 | 4 | 1004 | 130 | T/X | 0.7 | 11.5 | 2.17 | N/S | N/S | 339.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2024-12-30 | 4.1 | 7.1 | 7.7 | 5 | 3 | <5 | 6 | 4 | 788 | <50 | T/X | <0.3 | 9.45 | 1.47 | <0.005 | <5 | 282.44 | 0.6 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | 0.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2024-12-31 | 4.1 | 7.2 | 7.7 | T/X | T/X | N/S | 13 | 11 | 840 | 86 | T/X | T/X | T/X | T/X | N/S | N/S | 289.25 | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.007 | 0.1 | N/S | <0.002 | 0.01 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.6 | N/S
RL effective 1/1/24 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 25 | 1 | 0.3 | 0.5 | 0.15 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
Observations | 366 | 366 | 366 | 182 | 182 | 53 | 365 | 365 | 366 | 366 | 62 | 249 | 250 | 251 | 53 | 51 | 182 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 49 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 0 | 0 | 0 | 52 | 33
Minimum | 1.33 | 7.1 | 7.1 | <2 | <2 | <5 | <4 | <4 | 470 | <50 | <4 | <0.3 | 6.76 | 0.4 | <0.005 | <5 | 130.3 | 0.5 | 700 | <0.002 | 0.022 | <0.002 | <0.004 | 0.002 | 0.03 | 0.02 | <0.002 | 0.002 | <0.002 | <0.004 | <0.004 | 0.016 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | <0.5 | 6
Mean | 2.7039 | 7.4003 | 8.5235 | <6 | <2 | <4 | <5 | <5 | 1117.4699 | <182 | <3 | <0.4 | 15.3618 | 2.448 | <0.004 | <4 | 343.2258 | 0.81321 | GM=6075 | <0.001 | 0.036264 | <0.001 | <0.003 | 0.0058974 | 0.073585 | 0.034255 | <0.002 | 0.01102 | <0.001 | <0.003 | <0.003 | 0.025981 | <0.001 | <0.001 | <0.001 | <2 |  |  |  | <0.9 | 7.4848
Maximum | 7.97 | 7.6 | 10.2 | 26 | 10 | <5 | 30 | 26 | 2732 | 526 | 9 | 4.3 | 25.03 | 4.07 | 0.009 | 24 | 1309.61 | 1.1 | 540000 | <0.002 | 0.058 | <0.002 | <0.004 | 0.024 | 0.42 | 0.06 | 0.05 | 0.045 | 0.003 | <0.004 | <0.004 | 0.049 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | 6.3 | 14
%>400=100
Note: Highlighted cells indicate revisions made.
January 7, 18, 2024, NO2-N + NO3-N: Sample MS/MSD recovery failed but LCS passed.
January 8, 2024, FOG: Sample MS/MSD recovery failed but LCS passed.
January 8 - 11, 17, 18, 2024, BOD5, CBOD5, T/X: Incubator failure.
January 8, 2024, Cr6+, T/X: Filtered LCS failure.
January 14, 2024, TKN, NH3-N, NO2-N + NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
January 21, 2024, NH3-N, NO2-N + NO3-N: Sample MS/MSD recovery failed but LCS passed.
February 8, 2024, TKN, NH3-N, P-TOT: Sample MS/MSD recovery failed but LCS passed.
February 11, 18, 2024, TKN, NH3-N, NO2-N + NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
February 14, 15, 2024, BOD5, CBOD5, T/X: Method blank failure.
February 19, 20, 26, 27, 2024, BOD5, CBOD5, T/X: GGA failure.
February 25, 2024, NH3-N, NO2-N + NO3-N: Sample MS/MSD recovery failed but LCS passed.
February 26, 2024, TKN: Sample MS/MSD recovery failed but LCS passed.
March 3, 2024, SS, VSS, T/X: VSS was greater than TSS.
March 6, 18, 20, 31, 2024, TKN: Sample MS/MSD recovery failed but LCS passed.
March 11, 2024, Cr6+, T/X: Filtered LCS failure.
March 25-28, 31, 2024, TKN,T/X: Expired reagent used.
March 26, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
April 1-4, 7-11, 14-18, 21-25, 28-30, 2024, TKN,T/X: Expired reagent used.
April 3, 4, 2024, BOD5, CBOD5, T/X: Seed control failure.
April 16, 29, 2024, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
April 18, 2024, NO2-N+NO3-N, T/X: Duplicate failure, rerun did not confirm either result.
April 21, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
May 1, 5-9, 12, 14-16, 19-23, 27-30, 2024, TKN,T/X: Expired reagent used.
May 2, 13, 2024, TKN, NH3-N, T/X: NH3>TKN, confirmation test not completed.
May 8, 2024, TKN: Sample MS/MSD recovery failed but LCS passed.
May 14, 19, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
May 20, 21, 2024, BOD5, CBOD5, T/X: GGA failure.
May 21, 22, 23, 2024, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
May 26, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
June 2-6, 9-13, 16, 17, 19, 20, 23-27, 30, 2024, TKN,T/X: Expired reagent used.
June 4, 19, 20, 23, P-TOT: Sample MS/MSD recovery failed but LCS passed.
June 6, 2024, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
June 9, 10, 2024, NH3-N: Sample MS/MSD recovery failed but LCS passed.
June 10, 11, 18, 20, 2024, BOD5, CBOD5, T/X: Incubator failure.
June 12, 17, 19, 2024, BOD5, CBOD5, T/X: LCS failure.
June 18, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
June 25, 2025, BOD5, CBOD5, T/X: Broken sample container.
June 27, 2024, BOD5, CBOD5, T/X: GGA failure.
July 1, 2, 4, 7-11, 14-18, 21-25, 28-31, 2024, TKN,T/X: Expired reagent used.
July 1, 8, 2024, PHENOL, T/X: LOQ verification failure.
July 3, 2024, BOD5, CBOD5, T/X: Test cancelled for holiday.
July 3, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
July 7, 14, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
July 23, 2024, NH3-N: Sample MS/MSD recovery failed but LCS passed.
July 29, 2024, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
August 1, 4-8, 11-15, 18-22, 25-29, 2024, TKN,T/X: Expired reagent used.
August 5, 2024, NH3-N: Sample MS/MSD recovery failed but LCS passed.
August 18, 22, 28, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
August 29, 2024, TKN: Sample MS/MSD recovery failed but LCS passed.
September 2-5, 8-12, 15-19, 22-26, 29, 30, 2024, TKN,T/X: Expired reagent used.
September 1, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
September 2, 2024, PHENOL: Sample MS/MSD recovery failed but LCS passed.
September 3, 2024, Hg LL, S/X: BrCl preservative was contaminated.
September 11, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
October 1-3, 6-10, 13-17, 20-24, 27-31, 2024, TKN,T/X: Expired reagent used.
October 2, 8, 13, 2024, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
October 2, 3, 15, 27, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
October 13, 2024, NH3-N: Sample MS/MSD recovery failed but LCS passed.
November 3-7, 11-14, 17-21, 24-26, 28, 2024, TKN,T/X: Expired reagent used.
November 10, 27, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
November 24, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
December 1-5, 8-12, 15-19, 22, 23, 25, 26, 29, 30, 2024, TKN,T/X: Expired reagent used.
December 2, 2024, Phenol: Sample MS/MSD recovery failed but LCS passed.
December 3, 2024, Fe-S: Sample MS recovery failed but LCS passed.
December 15, 2024, P-TOT: Sample MS/MSD recovery failed but LCS passed.
December 24, 31, 2024, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Sample aliquot not preserved within required holding time due to holiday.
December 24, 31, 2024, BOD5, CBOD5, T/X: Courrier not scheduled due to holiday.

## Lemont Outfall 2025
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2025-01-01 | 4.1 | 7.3 | 8.6 | 11 | 5 | N/S | 8 | 6 | 860 | 100 | T/X | <0.300 | 10.04 | 1.35 | N/S | N/S | 272.993 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-02 | 4.1 | 7.2 | 8.2 | 16 | 6 | N/S | 11 | 10 | 888 | 88 | T/X | 2.1 | 9.69 | 2 | N/S | N/S | 283.713 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-03 | 2.77 | 7.4 | 8.2 | N/S | N/S | N/S | 11 | 10 | 1104 | 194 | N/S | N/S | N/S | N/S | N/S | N/S | 324.674 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-04 | 2.47 | 7.4 | 9 | N/S | N/S | N/S | 8 | 8 | 1062 | 140 | N/S | N/S | N/S | N/S | N/S | N/S | 316.097 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-05 | 2.4 | 7.4 | 8.7 | N/S | N/S | N/S | 13 | 11 | 1030 | 122 | T/X | 1.18 | 16.54 | 2.84 | N/S | N/S | 306.512 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-06 | 2.27 | 7.5 | 8.6 | 9 | 4 | <5 | 11 | 9 | 1050 | 132 | T/X | 0.47 | 17.41 | 2.85 | <0.005 | <5 | 319.074 | 0.919 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-01-07 | 2.25 | 7.4 | 8.9 | T/X | T/X | N/S | <4 | <4 | 1134 | 144 | T/X | <0.300 | 18.67 | 2.65 | N/S | N/S | 353.274 | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.008 | 0.11 | 0.03 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-01-08 | 2.21 | 7.4 | 9.2 | 9 | 4 | N/S | 8 | 7 | 1136 | 172 | T/X | <0.300 | 18.87 | 2.85 | N/S | N/S | 338.592 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-09 | 2.15 | 7.4 | 8.9 | 7 | 3 | N/S | 10 | 9 | 1050 | 142 | T/X | <0.300 | 20.59 | 2.83 | N/S | N/S | 295.577 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-10 | 2.14 | 7.4 | 9.2 | N/S | N/S | N/S | <4 | <4 | 1094 | 128 | N/S | N/S | N/S | N/S | N/S | N/S | 336.626 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-11 | 2.3 | 7.5 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1458 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | 518.617 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-12 | 2.27 | 7.5 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1490 | 164 | T/X | 2.19 | 15.15 | 2.93 | N/S | N/S | 544.947 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-13 | 1.95 | 7.4 | 8.6 | 6 | 3 | <5 | <4 | <4 | 1046 | 180 | T/X | 0.65 | 17.26 | 2.78 | <0.005 | <5 | 615.402 | 0.952 | 31000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-01-14 | 2.19 | 7.4 | 9 | 10 | 5 | N/S | 6 | 4 | 1414 | 204 | T/X | <0.300 | 19.11 | 2.84 | N/S | N/S | 556.592 | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.006 | 0.08 | 0.05 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-01-15 | 2.1 | 7.3 | 9.6 | 9 | 3 | N/S | 7 | 5 | 1398 | 154 | T/X | <0.300 | 19.72 | 2.69 | N/S | N/S | 478.906 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-16 | 2.23 | 7.4 | 9.2 | 11 | 5 | N/S | 6 | 4 | 1172 | 494 | T/X | 0.31 | 17.92 | 2.7 | N/S | N/S | 466.545 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-17 | 2.1 | 7.5 | 8.7 | N/S | N/S | N/S | 5 | 4 | 1314 | 102 | N/S | N/S | N/S | N/S | N/S | N/S | 454.203 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-18 | 2.22 | 7.3 | 8.5 | N/S | N/S | N/S | 5 | 5 | 1312 | 106 | N/S | N/S | N/S | N/S | N/S | N/S | 479.398 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-19 | 2.2 | 7.3 | 8.7 | N/S | N/S | N/S | <4 | <4 | 1324 | 118 | T/X | T/X | T/X | T/X | N/S | N/S | 455.864 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-20 | 2.2 | 7.3 | 9 | 13 | 5 | <5 | 4 | 4 | 1300 | 152 | T/X | 0.34 | 20.06 | 2.89 | <0.005 | <5 | 408.083 | 0.988 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 12
2025-01-21 | 2.23 | 7.3 | 9 | 14 | 6 | N/S | 6 | 5 | 1250 | 134 | T/X | <0.300 | 20.11 | 2.82 | N/S | N/S | 395.623 | N/S | 110000 | <0.002 | 0.035 | <0.002 | <0.004 | 0.008 | 0.08 | 0.05 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 1 | N/S
2025-01-22 | 2.14 | 7.5 | 9.6 | 10 | 5 | N/S | 7 | 6 | 1238 | 186 | T/X | <0.300 | 20.01 | 2.59 | N/S | N/S | 391.074 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-23 | 2.14 | 7.4 | 8.9 | 13 | 5 | N/S | 9 | 8 | 1312 | 184 | T/X | <0.300 | 19.95 | 2.64 | N/S | N/S | 406.685 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-24 | 2.14 | 7.4 | 9.1 | N/S | N/S | N/S | 4 | <4 | 1226 | 258 | N/S | N/S | N/S | N/S | N/S | N/S | 410.622 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-25 | 1.98 | 7.4 | 8.9 | N/S | N/S | N/S | 5 | 4 | 1252 | 282 | N/S | N/S | N/S | N/S | N/S | N/S | 407.717 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-26 | 2.03 | 7.4 | 8.6 | N/S | N/S | N/S | 4 | 4 | 1266 | 136 | T/X | <0.300 | 18.42 | 2.87 | N/S | N/S | 377.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-27 | 2.23 | 7.3 | 8.4 | 7 | 3 | <5 | <4 | <4 | 1008 | 132 | T/X | 1.69 | 18.07 | 2.9 | <0.005 | <5 | 353.804 | 1.023 | 48000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 12
2025-01-28 | 2.5 | 7.3 | 8.4 | 13 | 5 | N/S | 4 | 4 | 1222 | 164 | T/X | 4 | 12.42 | 1.47 | N/S | N/S | 386.031 | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.007 | 0.08 | 0.05 | <0.002 | 0.019 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.5 | N/S
2025-01-29 | 2.04 | 7.5 | 8.4 | 9 | 4 | N/S | 4 | 4 | 1364 | 174 | T/X | 3.89 | 13.02 | 2.95 | N/S | N/S | 441.441 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-30 | 2.21 | 7.3 | 8.6 | 9 | 4 | N/S | 4 | <4 | 1442 | 188 | T/X | 1.83 | 15.66 | 2.84 | N/S | N/S | 480.812 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-01-31 | 3.84 | 7.2 | 8.4 | N/S | N/S | N/S | <4 | 4 | 1588 | 144 | N/S | N/S | N/S | N/S | N/S | N/S | 687.154 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-01 | 4.18 | 7 | 9.6 | N/S | N/S | N/S | 4 | 4 | 1484 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | 639.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-02 | 4.17 | 7.1 | 8.2 | N/S | N/S | N/S | 6 | 5 | 1348 | 110 | T/X | 3.9 | 5.81 | 1.53 | N/S | N/S | 557.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-03 | 2.84 | 7.4 | 8.2 | 9 | 4 | <5 | 6 | 5 | 1332 | 128 | T/X | 5.36 | 5.04 | 1.8 | <0.005 | <5 | 491.754 | 0.765 | 9400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-02-04 | 2.56 | 7.3 | 9.2 | 9 | 3 | N/S | <4 | <4 | 1352 | 118 | T/X | 1.02 | 10.82 | 2.03 | N/S | N/S | 513.947 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.007 | 0.07 | 0.03 | <0.002 | 0.017 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.1 | N/S
2025-02-05 | 2.49 | 7.2 | 9.7 | 7 | 3 | N/S | 6 | 4 | 1324 | 126 | T/X | 0.83 | 14.55 | 2.32 | N/S | N/S | 483.049 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-06 | 2.41 | 7.3 | 8.8 | 14 | 4 | N/S | 6 | 5 | 1304 | 104 | T/X | 1.82 | 14.23 | 2.62 | N/S | N/S | 484.825 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-07 | 2.3 | 7.4 | 9.1 | N/S | N/S | N/S | <4 | <4 | 1062 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | 465.659 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-08 | 2.32 | 7.5 | 8.9 | N/S | N/S | N/S | <4 | <4 | 1226 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | 428.648 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-09 | 2.29 | 7.5 | 8.3 | N/S | N/S | N/S | 6 | 6 | 964 | 104 | T/X | 3.74 | 12.08 | 2.62 | N/S | N/S | 381.973 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-10 | 2.21 | 7.4 | 8.9 | 4 | <2 | <5 | <4 | <4 | 1070 | 72 | T/X | 3.61 | 12.59 | 2.53 | <0.005 | 6 | 350.936 | 0.961 | 1400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-02-11 | 2.16 | 7.5 | 9.2 | T/X | T/X | N/S | 6 | 5 | 1150 | 280 | T/X | T/X | T/X | T/X | N/S | N/S | 395.656 | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | N/S | T/X | T/X | T/X | T/X | <0.004 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | 1 | N/S
2025-02-12 | 2.16 | 7.5 | 9 | 11 | 4 | N/S | 7 | 6 | 1206 | 186 | T/X | 1.14 | 17.35 | 2.61 | N/S | N/S | 424.022 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-13 | 2.14 | 7.4 | 9.1 | 12 | 5 | N/S | 5 | 4 | 1254 | 56 | T/X | 1.33 | 17.91 | 2.55 | N/S | N/S | 496.536 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-14 | 2.09 | 7.3 | 9.2 | N/S | N/S | N/S | 7 | 5 | 1320 | 76 | N/S | N/S | N/S | N/S | N/S | N/S | 472.304 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-15 | 2.19 | 7.3 | 8.9 | N/S | N/S | N/S | 7 | 6 | 1446 | 86 | N/S | N/S | N/S | N/S | N/S | N/S | 554.295 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-16 | 2.19 | 7.4 | 8.9 | N/S | N/S | N/S | 7 | 6 | 1564 | 76 | T/X | T/X | T/X | T/X | N/S | N/S | 642.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-17 | 2.19 | 7.2 | 9.2 | 21 | 5 | <5 | 7 | 6 | 1458 | 108 | T/X | 3.1 | 15.04 | 2.71 | 0.005 | 6 | 567.306 | 0.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 12
2025-02-18 | 2.12 | 7.4 | 9.2 | 13 | 5 | N/S | 4 | <4 | 1346 | 82 | T/X | 1.71 | 17.18 | 2.64 | N/S | N/S | 521.376 | N/S | 3700 | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | <0.004 | T/X | T/X | T/X | T/X | <3 | N/S | N/S | N/S | 1.1 | N/S
2025-02-19 | 2.14 | 7.4 | 9.3 | 14 | 5 | N/S | 7 | 6 | 1280 | 142 | T/X | 1.09 | 17.73 | 2.58 | N/S | N/S | 463.202 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-20 | 2.14 | 7.3 | 9.2 | 12 | 5 | N/S | 7 | 7 | 1198 | 200 | T/X | 0.99 | 18.31 | 2.7 | N/S | N/S | 420.371 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-21 | 2.12 | 7.4 | 9.4 | N/S | N/S | N/S | <4 | <4 | 1150 | 168 | N/S | N/S | N/S | N/S | N/S | N/S | 384.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-22 | 2.2 | 7.5 | 8.8 | N/S | N/S | N/S | <4 | <4 | 1160 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | 387.032 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-23 | 2.2 | 7.5 | 9 | N/S | N/S | N/S | <4 | <4 | 1268 | 228 | T/X | 4.13 | 13.75 | 2.61 | N/S | N/S | 386.397 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-24 | 1.92 | 7.4 | 8.5 | 10 | 2 | <5 | 5 | 4 | 1190 | 114 | T/X | 2.55 | 14.79 | 2.63 | <0.005 | <5 | 394.001 | 1.02 | 56000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-02-25 | 2.38 | 7.3 | 8.5 | 13 | 5 | N/S | 7 | 6 | 1424 | 110 | T/X | 1.37 | 16.31 | 2.62 | N/S | N/S | 540.292 | N/S | N/S | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | T/X | <0.004 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-02-26 | 2.33 | 7.4 | 8.5 | 13 | 5 | N/S | 10 | 9 | 848 | 118 | T/X | 1.13 | 17.26 | 2.64 | N/S | N/S | 619.306 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-27 | 2.41 | 7.3 | 8.5 | 13 | 6 | N/S | 13 | 11 | 1540 | 118 | T/X | 1.75 | 17.4 | 2.84 | N/S | N/S | 627.427 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-02-28 | 2.31 | 7.3 | 8.5 | N/S | N/S | N/S | 10 | 9 | 1500 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | 601.715 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-01 | 2.43 | 7.3 | 8.6 | N/S | N/S | N/S | 10 | 9 | 1512 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | 549.448 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-02 | 2.48 | 7.3 | 8.9 | N/S | N/S | N/S | 6 | 5 | 1396 | 128 | 3.2 | 2.46 | 16.15 | 3.17 | N/S | N/S | 507.026 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-03 | 2.82 | 7.3 | 8.4 | 26 | 9 | <5 | 13 | 12 | 1256 | 136 | 7.1 | 4.81 | 11.9 | 3.05 | <0.005 | <5 | 438.485 | 0.969 | 7400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 16
2025-03-04 | 3.46 | 7.4 | 8.7 | 20 | 9 | N/S | 11 | 10 | 1282 | 138 | 5.6 | 3.72 | 9.41 | 2.28 | N/S | N/S | 532.277 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.009 | 0.11 | 0.05 | <0.002 | 0.059 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2025-03-05 | 4.1 | 7.2 | 8.4 | 7 | 4 | N/S | 6 | 5 | 1186 | 132 | 1.4 | <0.300 | 8.73 | 0.96 | N/S | N/S | 515.903 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-06 | 4.1 | 7.2 | 9.8 | 5 | 3 | N/S | 6 | 6 | 1192 | 82 | <1.000 | <0.300 | 9.98 | 0.85 | N/S | N/S | 515.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-07 | 4.1 | 7.2 | 9 | N/S | N/S | N/S | <4 | <4 | 1280 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 516.788 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-08 | 4.1 | 7.3 | 8.3 | N/S | N/S | N/S | <4 | <4 | 1400 | 202 | N/S | N/S | N/S | N/S | N/S | N/S | 528.198 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-09 | 3.93 | 7.3 | 8 | N/S | N/S | N/S | <4 | <4 | 1306 | 122 | 4.5 | 2.57 | 8.8 | 1.42 | N/S | N/S | 501.213 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-10 | 4.1 | 7.2 | 8 | 10 | 3 | <5 | 4 | 5 | 1312 | 128 | 7.6 | 5.19 | 6.57 | 1.59 | 0.005 | <5 | 488.598 | 0.716 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-03-11 | 2.7 | 7.4 | 8.4 | <2 | <2 | N/S | 5 | 5 | 1526 | 282 | 6.1 | 3.95 | 7.83 | 1.86 | N/S | N/S | 525.441 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.005 | 0.07 | 0.04 | <0.002 | 0.029 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-03-12 | 2.15 | 7.4 | 9.1 | 10 | 3 | N/S | 4 | 4 | 1352 | 124 | <4.000 | 0.56 | 13.57 | 2.12 | N/S | N/S | 515.842 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-13 | 2.73 | 7.3 | 9 | 12 | 5 | N/S | 5 | <4 | 1354 | 194 | 1.8 | 1.54 | 14.81 | 2.25 | N/S | N/S | 469.213 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-14 | 2.42 | 7.4 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1262 | 136 | N/S | N/S | N/S | N/S | N/S | N/S | 456.867 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-15 | 3.25 | 7.3 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1192 | 144 | N/S | N/S | N/S | N/S | N/S | N/S | 431.179 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-16 | 3.45 | 7.2 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1268 | 138 | <4.000 | <0.300 | 11.34 | 1.3 | N/S | N/S | 460.444 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-17 | 3.71 | 7.2 | 8.7 | 5 | 4 | <5 | 8 | 7 | 1274 | 150 | 2.9 | 0.62 | 11.35 | 1.44 | <0.005 | <5 | 458.535 | 0.704 | 5800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-03-18 | 3.42 | 7.2 | 8.6 | 11 | 13 | N/S | 19 | 17 | 1272 | 152 | 3.2 | 0.91 | 10.67 | 1.79 | N/S | N/S | 440.422 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.011 | 0.17 | 0.03 | <0.002 | 0.02 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-03-19 | 3.47 | 7.2 | 8 | 12 | 8 | N/S | 12 | 10 | 1140 | 132 | 1.8 | 0.55 | 11.01 | 1.79 | N/S | N/S | 415.735 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-20 | 4.1 | 7.3 | 9.7 | 8 | 4 | N/S | 11 | 6 | 1124 | 146 | 1.5 | <0.300 | 9.21 | 1.07 | N/S | N/S | 459.187 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-21 | 4.1 | 7.3 | 9.5 | N/S | N/S | N/S | <4 | <4 | 1100 | 138 | N/S | N/S | N/S | N/S | N/S | N/S | 428.456 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-22 | 4.1 | 7.4 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1108 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 405.683 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-23 | 4.1 | 7.3 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1122 | 176 | <4.000 | <0.300 | 10.83 | 1.31 | N/S | N/S | 399.159 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-24 | 4.1 | 7.2 | 8.4 | 4 | <2 | T/X | <4 | <4 | 714 | 94 | <4.000 | 0.32 | 11 | 1.25 | <0.005 | <5 | 400.329 | 0.657 | 3100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-03-25 | 4.1 | 7.3 | 8.1 | 8 | 3 | N/S | 4 | <4 | 1180 | 164 | 2.2 | 2.31 | 9.39 | 1.59 | N/S | N/S | 418.584 | 0.691 | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.005 | 0.08 | 0.04 | <0.002 | 0.02 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.9 | N/S
2025-03-26 | 2.86 | 7.3 | 8.2 | 11 | 4 | N/S | 10 | 8 | 1206 | 162 | 3.4 | 1.51 | 9.83 | 2.07 | N/S | N/S | 391.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-27 | 2.71 | 7.3 | 8.6 | 12 | 4 | N/S | 8 | 6 | 1158 | 132 | <4.000 | 0.64 | 13.94 | 1.99 | N/S | N/S | 386.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-28 | 2.73 | 7.3 | 8.4 | N/S | N/S | N/S | 7 | 6 | 1106 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 368.418 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-29 | 2.75 | 7.3 | 8.5 | N/S | N/S | N/S | 6 | 5 | 1166 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | 369.721 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-30 | 2.75 | 7.3 | 8.1 | N/S | N/S | N/S | 6 | 5 | 1132 | 132 | <4.000 | <0.300 | 14.84 | 1.95 | N/S | N/S | 344.808 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-03-31 | 3.27 | 7.2 | 8.6 | 12 | 4 | <5 | 9 | 8 | 1186 | 180 | <4.000 | 0.7 | 13.12 | 1.62 | <0.005 | <5 | 353.971 | 0.743 | 69000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | 9
2025-04-01 | 2.68 | 7.4 | 7.8 | 13 | 5 | N/S | 11 | 7 | 1180 | 130 | 1.7 | 0.65 | 11.07 | 1.94 | N/S | N/S | 367.969 | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.008 | 0.11 | 0.03 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2025-04-02 | 3.63 | 7.4 | 9 | 7 | 5 | N/S | 10 | 7 | 796 | 76 | 2.5 | <0.300 | 8.32 | 1.49 | N/S | N/S | 250.357 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-03 | 4.1 | 7.3 | 9.8 | <2 | <2 | N/S | <4 | <4 | 836 | 118 | <1.000 | <0.300 | 6.75 | 0.76 | N/S | N/S | 259.882 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-04 | 4.06 | 7.3 | 9.6 | N/S | N/S | N/S | <4 | <4 | 998 | 138 | N/S | N/S | N/S | N/S | N/S | N/S | 333.219 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-05 | 4.1 | 7.4 | 9 | N/S | N/S | N/S | <4 | <4 | 990 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 334.501 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-06 | 4.1 | 7.5 | 8.9 | N/S | N/S | N/S | <4 | <4 | 916 | 70 | <1.000 | <0.300 | 9.37 | 0.81 | N/S | N/S | 325.935 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-07 | 4.1 | 7.3 | 8.6 | 3 | <2 | <5 | <4 | <4 | 990 | 98 | <1.000 | <0.300 | 9.99 | 1 | <0.005 | <5 | 316.223 | 0.602 | 23000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-04-08 | 4.1 | 7.3 | 9.3 | 9 | 4 | N/S | 8 | 6 | 1032 | 158 | <1.000 | <0.300 | 9.54 | 1.15 | N/S | N/S | 337.504 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.006 | 0.08 | 0.03 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2025-04-09 | 4.1 | 7.3 | 8.5 | 10 | 4 | N/S | 4 | <4 | 1062 | 152 | 1.9 | 0.56 | 10.72 | 1.29 | N/S | N/S | 323.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-10 | 4.1 | 7.3 | 8 | 10 | 5 | N/S | <4 | <4 | 958 | 138 | 2 | 0.75 | 10.44 | 1.36 | N/S | N/S | 288.132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-11 | 4.1 | 7.3 | 9.3 | N/S | N/S | N/S | 6 | 5 | 876 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | 257.709 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-12 | 4.07 | 7.3 | 7.6 | N/S | N/S | N/S | 4 | 5 | 976 | 130 | N/S | N/S | N/S | N/S | N/S | N/S | 268.324 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-13 | 2.8 | 7.4 | 7.7 | N/S | N/S | N/S | 4 | 4 | 980 | 108 | 6.3 | 4.97 | 6.73 | 1.93 | N/S | N/S | 275.796 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-14 | 2.64 | 7.3 | 8.4 | 7 | 2 | <5 | <4 | <4 | 1052 | 106 | 5.1 | 1.22 | 12.18 | 1.81 | <0.005 | <5 | 298.642 | 0.846 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-04-15 | 2.56 | 7.4 | 8.7 | 5 | <2 | N/S | <4 | <4 | 1114 | 120 | 2.3 | 0.79 | 13.94 | 1.94 | N/S | N/S | 311.049 | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.004 | 0.05 | 0.03 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.022 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-04-16 | 2.42 | 7.4 | 9 | T/X | T/X | N/S | <4 | <4 | 1100 | 140 | <4.000 | 0.6 | 14.57 | 2.16 | N/S | N/S | 317.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-17 | 2.42 | 7.4 | 8.7 | T/X | T/X | N/S | <4 | <4 | 1138 | 266 | <4.000 | 0.5 | 15.11 | 2.09 | N/S | N/S | 313.194 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-18 | 2.44 | 7.4 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1044 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | 306.591 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-19 | 2.71 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 980 | 190 | N/S | N/S | N/S | N/S | N/S | N/S | 280.077 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-20 | 3.3 | 7.4 | 7.9 | N/S | N/S | N/S | <4 | <4 | 980 | 126 | 2.2 | 2.75 | 9.87 | 1.68 | N/S | N/S | 287.123 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-21 | 3.68 | 7.4 | 7.6 | 4 | <2 | <5 | <4 | <4 | 1022 | 218 | 2.1 | 1.56 | 8.98 | 1.39 | <0.005 | <5 | 284.526 | 0.661 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | 8
2025-04-22 | 2.88 | 7.3 | 8.8 | 6 | 3 | N/S | 4 | <4 | 1098 | 190 | <4.000 | 0.62 | 11.34 | 1.57 | N/S | N/S | 362.135 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.004 | 0.04 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2025-04-23 | 3.69 | 7.3 | 8.6 | 10 | 5 | N/S | 4 | 4 | 986 | 132 | 2.9 | 0.77 | 9.95 | 1.84 | N/S | N/S | 344.551 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-24 | 2.83 | 7.3 | 8.2 | 5 | 3 | N/S | 5 | 5 | 1114 | 178 | <4.000 | <0.300 | 11.34 | 1.52 | N/S | N/S | 363.955 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-25 | 3.44 | 7.4 | 9 | N/S | N/S | N/S | 7 | 7 | 1046 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | 362.426 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-26 | 3.33 | 7.2 | 7.2 | N/S | N/S | N/S | 8 | 7 | 1054 | 184 | N/S | N/S | N/S | N/S | N/S | N/S | 337.972 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-27 | 2.68 | 7.2 | 7.4 | N/S | N/S | N/S | 5 | 4 | 1160 | 224 | 1.8 | 0.99 | 11.28 | 1.54 | N/S | N/S | 330.218 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-04-28 | 2.7 | 7.3 | 7.9 | 9 | 4 | <5 | 6 | 6 | 1234 | 288 | 1.58 | 1.03 | 11.66 | 1.89 | <0.005 | <5 | 309.298 | 0.788 | 5700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-04-29 | 2.68 | 7.3 | 7.7 | 9 | 4 | N/S | 5 | <4 | 1160 | 132 | 3.899 | 0.644 | 13.965 | 2.222 | N/S | N/S | 341.839 | N/S | N/S | <0.002 | 0.039 | <0.002 | <0.004 | 0.007 | 0.08 | 0.03 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2025-04-30 | 2.66 | 7.2 | 7.9 | 10 | 4 | N/S | 5 | 4 | 1184 | 212 | <4.000 | 1.026 | 12.849 | 2.056 | N/S | N/S | 347.821 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-01 | 3.14 | 7.3 | 7.9 | 12 | 5 | N/S | 4 | 4 | 1132 | 266 | <4.000 | 0.918 | 12.471 | 1.875 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-02 | 2.84 | 7.3 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1124 | 234 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-03 | 2.64 | 7.5 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1162 | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-04 | 2.64 | 7.5 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1088 | 160 | 2.026 | 1.371 | 12.852 | 2.176 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-05 | 2.62 | 7.4 | 8 | 8 | 3 | <5 | <4 | <4 | 1120 | 200 | 1.84 | 1.746 | 12.075 | 2.212 | 0.005 | <5 | 341.949 | 0.84 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-05-06 | 2.5 | 7.4 | 8.3 | 10 | 4 | N/S | 4 | 4 | 1340 | 208 | <4.000 | 1.402 | 11.207 | 2.322 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.042 | <0.002 | <0.004 | 0.004 | 0.06 | 0.03 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.5 | N/S
2025-05-07 | 2.44 | 7.4 | 8.2 | 5 | 3 | N/S | 5 | 4 | 1234 | 188 | 1.475 | 0.855 | 12.507 | 2.425 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-08 | 2.32 | 7.4 | 8.4 | 6 | 3 | N/S | <4 | <4 | 1240 | 168 | 1.963 | 0.818 | 13.264 | 2.301 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-09 | 2.31 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1268 | 206 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-10 | 2.28 | 7.4 | 8 | N/S | N/S | N/S | 4 | 4 | 1358 | 288 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-11 | 2.28 | 7.4 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1220 | 218 | 3.949 | 2.487 | 11.798 | 2.552 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-12 | 2.28 | 7.4 | 7.6 | 8 | 2 | <5 | <4 | <4 | 1046 | 86 | 2.793 | 2.806 | 10.857 | 2.768 | <0.005 | <5 | 301.844 | 0.912 | 1500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-05-13 | 2.26 | 7.4 | 7.6 | 8 | 2 | N/S | 4 | <4 | 1042 | 110 | 2.384 | 1.482 | 12.812 | 2.705 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.037 | <0.002 | <0.004 | 0.007 | 0.08 | 0.04 | <0.002 | 0.021 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2025-05-14 | 2.22 | 7.4 | 7.6 | <2 | <2 | N/S | <4 | <4 | 960 | 86 | <4.000 | 0.837 | 13.788 | 2.652 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-15 | 1.98 | 7.4 | 7.6 | 2 | <2 | N/S | <4 | <4 | 1026 | 156 | <4.000 | <0.300 | 14.496 | 2.586 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-16 | 1.14 | 7.4 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1022 | 174 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-17 | 2.25 | 7.5 | 7.9 | N/S | N/S | N/S | 4 | 4 | 1040 | 182 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-18 | 2.53 | 7.4 | 7.3 | N/S | N/S | N/S | 6 | 6 | 944 | 150 | 1.691 | 2.966 | 12.902 | 2.666 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-19 | 2.04 | 7.4 | 7.3 | 11 | 3 | <5 | 6 | 5 | 896 | 160 | 1.573 | 1.66 | 13.713 | 2.818 | <0.005 | <5 | 207.129 | 0.965 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-05-20 | 3.02 | 7.3 | 8.2 | 10 | 4 | N/S | 5 | 4 | 886 | 180 | 2.254 | 0.443 | 15.368 | 2.748 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.006 | 0.09 | 0.04 | <0.002 | 0.017 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2025-05-21 | 2.81 | 7.3 | 7.9 | 6 | 3 | N/S | <4 | <4 | 1004 | 162 | <4.000 | <0.300 | 14.468 | 2.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-22 | 2.52 | 7.3 | 8 | 6 | 3 | N/S | 7 | 5 | 1018 | 142 | <4.000 | <0.300 | 14.252 | 2.215 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-23 | 2.38 | 7.4 | 8.3 | N/S | N/S | N/S | 4 | 4 | 1062 | 164 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-24 | 2.32 | 7.4 | 7.9 | N/S | N/S | N/S | 5 | 5 | 1112 | 194 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-25 | 2.4 | 7.4 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1160 | 234 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-26 | 2.26 | 7.2 | 7.9 | 6 | 2 | <5 | 5 | 4 | 1126 | 200 | <4.000 | 0.917 | 12.983 | 2.478 | <0.005 | <5 | 301.266 | 0.915 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 9
2025-05-27 | 2.35 | 7.4 | 8 | 6 | 3 | N/S | 4 | <4 | 1132 | 186 | <4.000 | 1.269 | 13.245 | 2.518 | N/S | N/S | N/S | N/S | 2000 | <0.002 | 0.04 | <0.002 | <0.004 | 0.005 | 0.06 | 0.03 | <0.002 | 0.018 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | T/X | N/S
2025-05-28 | 2.86 | 7.4 | 8.1 | 10 | 4 | N/S | 6 | 5 | 1052 | 186 | 2.003 | 0.933 | 12.217 | 2.435 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-29 | 2.63 | 7.3 | 8 | 9 | 4 | N/S | <4 | 4 | 992 | 112 | <4.000 | 0.556 | 12.422 | 2.184 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-30 | 2.46 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1050 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-05-31 | 2.36 | 7.4 | 7.7 | N/S | N/S | N/S | 6 | 5 | 1104 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-01 | 2.39 | 7.5 | 7.2 | N/S | N/S | N/S | 5 | 4 | 1090 | 214 | 3.073 | 2.178 | 11.517 | 2.719 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-02 | 2.04 | 7.4 | 7.9 | 10 | 4 | <5 | 5 | 4 | 1094 | 114 | 2.257 | 1.754 | 11.351 | 2.797 | <0.005 | <5 | 311.245 | 0.961 | 2700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | 11
2025-06-03 | 2.17 | 7.4 | 7.3 | 9 | 4 | N/S | <4 | <4 | 1164 | 152 | 2.176 | 1.247 | 13.16 | 2.881 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.005 | 0.07 | 0.03 | <0.002 | 0.019 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.3 | N/S
2025-06-04 | 3.56 | 7.3 | 7.4 | 9 | 4 | N/S | <4 | <4 | 928 | 148 | 2.181 | 0.448 | 11.649 | 2.313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-05 | 4.09 | 7.2 | 7.6 | 6 | 3 | N/S | 6 | 5 | 980 | 160 | 1.515 | 0.543 | 10.418 | 1.559 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-06 | 2.34 | 7.4 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1104 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-07 | 2.33 | 7.3 | 7.3 | N/S | N/S | N/S | <4 | <4 | 1136 | 224 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-08 | 2.13 | 7.3 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1182 | 254 | <4.000 | <0.300 | 17.667 | 2.519 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-09 | 3.16 | 7.4 | 8.4 | 14 | 4 | <5 | 7 | 6 | 1128 | 176 | 4.374 | 3.212 | 12.302 | 2.466 | <0.005 | <5 | 341.055 | 0.859 | 30000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-06-10 | 2.86 | 7.4 | 6.9 | 13 | 5 | N/S | 4 | <4 | 1134 | 144 | 5.789 | 4.474 | 8.904 | 2.318 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.005 | 0.06 | 0.03 | <0.002 | 0.017 | <0.002 | <0.004 | <0.004 | 0.029 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2025-06-11 | 2.33 | 7.4 | 7.8 | T/X | T/X | N/S | 4 | <4 | 1364 | 262 | 1.95 | <0.300 | 14.86 | 2.738 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-12 | 2.01 | 7.4 | 7.9 | T/X | T/X | N/S | <4 | <4 | 1276 | 210 | <4.000 | <0.300 | 16.366 | 2.723 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-13 | 2.19 | 7.4 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1324 | 242 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-14 | 2.28 | 7.4 | 6.5 | N/S | N/S | N/S | 4 | 4 | 1454 | 252 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-15 | 2.28 | 7.4 | 7.2 | N/S | N/S | N/S | 6 | 5 | 1334 | 182 | 6.805 | 6.329 | 7.726 | 2.679 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-16 | 2.07 | 7.4 | 7.2 | 18 | 4 | <5 | 8 | 7 | 1278 | 190 | 6.217 | 5.526 | 8.212 | 2.926 | <0.005 | <5 | 397.174 | 0.931 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-06-17 | 2.34 | 7.4 | 7.2 | 13 | 5 | N/S | 6 | 5 | 1374 | 230 | 8.342 | 7.273 | 7.443 | 2.857 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.045 | <0.002 | <0.004 | 0.005 | 0.07 | 0.05 | <0.002 | 0.033 | <0.002 | <0.004 | <0.004 | 0.023 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2025-06-18 | 2.41 | 7.3 | 6.8 | 21 | 5 | N/S | 6 | 6 | 1196 | 346 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-19 | 2.5 | 7.3 | 7.2 | 13 | 5 | N/S | 7 | 6 | 886 | 322 | 2.107 | 0.869 | 8.54 | 1.622 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-20 | 2.86 | 7.4 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1036 | 294 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-21 | 3 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1192 | 380 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-22 | 3 | 7.4 | 7.4 | N/S | N/S | N/S | 7 | 6 | 1292 | 430 | 3.152 | 2.813 | 7.913 | 1.513 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-23 | 2.92 | 7.4 | 7.2 | T/X | T/X | <5 | 8 | 7 | 1042 | 186 | 6.878 | 4.758 | 8.533 | 2.338 | <0.005 | <5 | 313.092 | 0.724 | 8700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-06-24 | 2.86 | 7.3 | 7.1 | T/X | T/X | N/S | 4 | 4 | 1050 | 150 | 4.815 | 4.269 | 10.061 | 2.201 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.01 | 0.13 | 0.03 | <0.002 | 0.034 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2025-06-25 | 3 | 7.3 | 7.6 | 19 | 5 | N/S | <4 | <4 | 1050 | 210 | 2.615 | 3.161 | 10.771 | 0.984 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-26 | 3.37 | 7.3 | 7.3 | 6 | <2 | N/S | <4 | <4 | 1002 | 246 | <4.000 | 0.931 | 12.429 | 1.814 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-27 | 4.1 | 7.2 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1024 | 300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-28 | 4.06 | 7.3 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1140 | 270 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-29 | 2.73 | 7.4 | 6.6 | N/S | N/S | N/S | <4 | <4 | 1336 | 322 | 2.341 | 2.245 | 7.918 | 2.469 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-06-30 | 2.49 | 7.3 | 7.7 | 7 | 3 | <5 | 6 | 4 | 1372 | 250 | <4.000 | 0.528 | 14.547 | 2.417 | <0.005 | <5 | 411.043 | 0.861 | 3100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-07-01 | 2.41 | 7.3 | 7.8 | 4 | 2 | N/S | 6 | 5 | 1434 | 266 | <4.000 | 0.437 | 16.202 | 2.513 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.048 | <0.002 | <0.004 | 0.003 | 0.05 | 0.03 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.024 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | T/X | N/S
2025-07-02 | 2.48 | 7.3 | 8.2 | 6 | 3 | N/S | 9 | 7 | 1440 | 344 | <4.000 | 0.32 | 16.109 | 2.623 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-03 | 2.37 | 7.4 | 8.3 | T/X | T/X | N/S | 8 | 5 | 1256 | 222 | <4.000 | 0.456 | 16.013 | 2.667 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-04 | 2.34 | 7.5 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1154 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-05 | 2.23 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1198 | 230 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-06 | 2.31 | 7.4 | 7.5 | N/S | N/S | N/S | 7 | 6 | 1208 | 192 | <4.000 | 0.318 | 17.509 | 2.571 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-07 | 2.57 | 7.3 | 7.7 | 5 | 4 | <5 | 8 | 6 | 1252 | 308 | 2.155 | 0.366 | 15.044 | 2.621 | <0.005 | <5 | 347.922 | 0.881 | 25000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-07-08 | 2.44 | 7.4 | 7.7 | 6 | 5 | N/S | 6 | 6 | 1400 | 274 | <4.000 | 0.401 | 14.328 | 2.235 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.05 | <0.002 | <0.004 | 0.005 | 0.08 | 0.03 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.1 | N/S
2025-07-09 | 2.48 | 7.4 | 8 | 4 | 3 | N/S | <4 | <4 | 1270 | 208 | <4.000 | 0.401 | 17.224 | 2.333 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-10 | 2.58 | 7.3 | 7.6 | 4 | 2 | N/S | <4 | <4 | 1258 | 174 | <4.000 | 0.569 | 16.324 | 2.335 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-11 | 4.04 | 7.2 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1266 | 534 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-12 | 3.84 | 7.3 | 6.8 | N/S | N/S | N/S | <4 | <4 | 1494 | 604 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-13 | 2.37 | 7.4 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1694 | 662 | <4.000 | 0.321 | 15.649 | 1.991 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-14 | 2.46 | 7.4 | 8 | 6 | 3 | <5 | 7 | 6 | 1240 | 212 | <4.000 | <0.300 | 18.573 | 2.339 | <0.005 | <5 | 345.197 | 0.852 | 6800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-07-15 | 2.44 | 7.4 | 8.2 | 4 | 3 | N/S | <4 | <4 | 1338 | 326 | <4.000 | <0.300 | 18.066 | 2.332 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.005 | 0.05 | 0.03 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.9 | N/S
2025-07-16 | 2.96 | 7.4 | 7.7 | 6 | 4 | N/S | 5 | 4 | 1110 | 192 | <4.000 | 0.381 | 16.14 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-17 | 2.35 | 7.3 | 7.6 | 7 | 4 | N/S | <4 | <4 | 986 | 176 | <4.000 | 0.475 | 12.709 | 2.052 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-18 | 3.12 | 7.3 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1318 | 330 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-19 | 3.11 | 7.4 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1268 | 356 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-20 | 2.82 | 7.3 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1116 | 290 | <4.000 | 0.319 | 12.888 | 1.771 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-21 | 2.53 | 7.3 | 8 | 4 | <2 | <5 | <4 | <4 | 1104 | 298 | <4.000 | 0.347 | 15.906 | 1.983 | <0.005 | <5 | 272.638 | 0.798 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-07-22 | 2.53 | 7.4 | 7.4 | 4 | 2 | N/S | <4 | <4 | 1130 | 190 | <4.000 | <0.300 | 17.193 | 2.178 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.005 | 0.07 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.1 | N/S
2025-07-23 | 2.51 | 7.3 | 7.9 | 4 | 2 | N/S | <4 | <4 | 1090 | 248 | <4.000 | <0.300 | 18.465 | 2.373 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-24 | 2.98 | 7.4 | 7.3 | 5 | 3 | N/S | <4 | <4 | 1000 | 214 | <4.000 | <0.300 | 17.797 | 2.353 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-25 | 4.04 | 7.2 | 7.5 | N/S | N/S | N/S | <4 | <4 | 766 | 180 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-26 | 4.1 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 764 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-27 | 4.1 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | 4 | 904 | 198 | <4.000 | <0.300 | 8.653 | 1.018 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-28 | 4.03 | 7.3 | 7.9 | 2 | <2 | <5 | <4 | <4 | 1058 | 282 | <4.000 | <0.300 | 10.657 | 1.416 | <0.005 | <5 | 235.963 | 0.56 | 71000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 7
2025-07-29 | 4.1 | 7.4 | 8.1 | <2 | <2 | N/S | <4 | <4 | 982 | 248 | <4.000 | <0.300 | 10.183 | 1.332 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.004 | 0.05 | 0.03 | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2025-07-30 | 4.05 | 7.4 | 8.3 | 3 | 2 | N/S | <4 | <4 | 1012 | 272 | <4.000 | <0.300 | 11.159 | 1.606 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-07-31 | 4.1 | 7.4 | 8.1 | 4 | <2 | N/S | <4 | <4 | 1028 | 200 | <4.000 | <0.300 | 12.483 | 1.556 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-01 | 3.9 | 7.3 | 7.9 | N/S | N/S | N/S | <4 | 4 | 1188 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-02 | 2.89 | 7.3 | 7.7 | N/S | N/S | N/S | 4 | 4 | 1260 | 204 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-03 | 2.45 | 7.4 | 8.4 | N/S | N/S | N/S | 4 | 4 | 1298 | 210 | <4.000 | <0.300 | 16.23 | 2.291 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-04 | 2.45 | 7.4 | 8 | 5 | 3 | <5 | 4 | <4 | 1300 | 312 | <4.000 | <0.300 | 17.656 | 2.461 | 0.005 | <5 | 299.371 | 0.845 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-08-05 | 2.88 | 7.3 | 7.4 | 5 | 3 | N/S | <4 | 4 | 1400 | 382 | <4.000 | 0.488 | 15.96 | 2.267 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.004 | 0.06 | 0.03 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2025-08-06 | 2.42 | 7.4 | 8 | 4 | 3 | N/S | 5 | <4 | 1330 | 316 | <4.000 | <0.300 | 16.724 | 2.408 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-07 | 4.43 | 7.4 | 8 | 3 | 2 | N/S | <4 | <4 | 1456 | 358 | <4.000 | 0.313 | 18.21 | 2.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-08 | 2.34 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 1454 | 348 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-09 | 2.19 | 7.5 | 6.7 | N/S | N/S | N/S | 4 | 4 | 1546 | 412 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-10 | 2.17 | 7.5 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1370 | 242 | <4.000 | 0.445 | 19.13 | 2.843 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-11 | 2.3 | 7.4 | 7.8 | 5 | 3 | <5 | <4 | <4 | 1338 | 234 | <4.000 | 0.494 | 18.263 | 2.783 | 0.005 | <5 | 408.558 | 0.886 | 4900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-08-12 | 2.71 | 7.4 | 8 | 5 | 3 | N/S | <4 | 5 | 1138 | 234 | <4.000 | 0.745 | 16.711 | 2.488 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.004 | 0.06 | 0.03 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-08-13 | 2.78 | 7.3 | 7.7 | 3 | 2 | N/S | <4 | <4 | 1150 | 254 | <4.000 | 0.365 | 15.344 | 2.076 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-14 | 2.47 | 7.4 | 7.7 | 3 | <2 | N/S | <4 | <4 | 1284 | 316 | <4.000 | 0.333 | 18.015 | 2.253 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-15 | 2.46 | 7.4 | 8 | N/S | N/S | N/S | <4 | <4 | 1286 | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-16 | 2.43 | 7.3 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1316 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-17 | 3.57 | 7.3 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1182 | 322 | <4.000 | <0.300 | 14.882 | 2.031 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-18 | 3.85 | 7.3 | 7.5 | 4 | 2 | <5 | 4 | <4 | 1020 | 156 | <4.000 | <0.300 | 12.021 | 1.576 | <0.005 | <5 | 284.849 | 0.636 | 74000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-08-19 | 4.1 | 7.2 | 7.5 | 3 | <2 | N/S | <4 | <4 | 854 | 208 | <1.000 | <0.300 | 9.695 | 1.127 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.004 | 0.05 | 0.02 | <0.002 | 0.005 | <0.002 | <0.004 | <0.004 | 0.065 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 10.5 | N/S
2025-08-20 | 4.09 | 7.4 | 7.7 | <2 | <2 | N/S | <4 | 4 | 932 | 200 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-21 | 4.1 | 7.4 | 7.8 | 3 | <2 | N/S | 4 | <4 | 1040 | 208 | <4.000 | <0.300 | 11.031 | 1.397 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-22 | 4.1 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1222 | 290 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-23 | 3.89 | 7.3 | 6.6 | N/S | N/S | N/S | <4 | <4 | 1084 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-24 | 2.45 | 7.5 | 6.9 | N/S | N/S | N/S | <4 | <4 | 1224 | 174 | 1.704 | 1.03 | 10.811 | 2.132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-25 | 2.33 | 7.4 | 7.6 | 4 | 3 | <5 | <4 | <4 | 1344 | 294 | <4.000 | <0.300 | 15.529 | 2.246 | <0.005 | <5 | 361.106 | 0.835 | 5900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-08-26 | 2.27 | 7.4 | 8.5 | 4 | 3 | N/S | 5 | 4 | 1350 | 280 | <4.000 | <0.300 | 17.332 | 2.385 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.006 | 0.07 | 0.03 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.03 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.1 | N/S
2025-08-27 | 2.26 | 7.5 | 7.1 | T/X | T/X | N/S | 4 | 4 | 1348 | 274 | <4.000 | <0.300 | 18.077 | 2.402 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-28 | 2.21 | 7.4 | 7.7 | T/X | T/X | N/S | 4 | 4 | 1090 | 164 | <4.000 | <0.300 | 20.164 | 2.499 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-29 | 2.26 | 7.5 | 8 | N/S | N/S | N/S | 4 | 4 | 1286 | 238 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-30 | 2.19 | 7.5 | 7.5 | N/S | N/S | N/S | 4 | <4 | 1322 | 248 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-08-31 | 2.1 | 7.4 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1212 | 204 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-01 | 2.08 | 7.5 | 8 | 4 | 3 | <5 | 5 | 4 | 1186 | 264 | <4.000 | <0.300 | 20.981 | 3.173 | <0.005 | <5 | 279.483 | 0.888 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 9
2025-09-02 | 2.19 | 7.5 | 7.6 | 5 | 3 | N/S | 4 | 4 | 1018 | 116 | <4.000 | <0.300 | 21.956 | 3.376 | N/S | N/S | N/S | N/S | 26000 | <0.002 | 0.038 | <0.002 | <0.004 | 0.007 | 0.13 | 0.03 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.037 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | <0.5 | N/S
2025-09-03 | 2.09 | 7.5 | 7.8 | 7 | 3 | N/S | 5 | 4 | 988 | 142 | <4.000 | 0.304 | 22.196 | 3.153 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-04 | 2.23 | 7.4 | 8 | 4 | 2 | N/S | <4 | <4 | 1010 | 204 | <4.000 | <0.300 | 21.192 | 2.961 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-05 | 2.01 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1122 | 330 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-06 | 2.02 | 7.5 | 7.3 | N/S | N/S | N/S | <4 | <4 | 1174 | 358 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-07 | 1.97 | 7.5 | 7.6 | N/S | N/S | N/S | 5 | 4 | 1102 | 330 | 1.315 | 0.472 | 21.919 | 3.194 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-08 | 1.98 | 7.4 | 8.1 | 4 | 2 | <5 | 5 | <4 | 1030 | 150 | <4.000 | 0.338 | 23.887 | 2.966 | <0.005 | <5 | 246.839 | 0.924 | 8200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-09-09 | 1.91 | 7.4 | 8.2 | <2 | <2 | N/S | <4 | <4 | 1088 | 202 | <4.000 | 0.369 | 22.98 | 2.899 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.004 | 0.04 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.044 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | T/X | N/S
2025-09-10 | 1.93 | 7.4 | 7.8 | 3 | <2 | N/S | <4 | <4 | 1104 | 262 | <4.000 | 0.339 | 23.773 | 3.575 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-11 | 1.96 | 7.4 | 7.8 | 4 | <2 | N/S | <4 | <4 | 1114 | 316 | <4.000 | 1.015 | 23.599 | 3.125 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-12 | 1.97 | 7.4 | 7.6 | N/S | N/S | N/S | 4 | <4 | 1074 | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-13 | 2.03 | 7.4 | 6.9 | N/S | N/S | N/S | 5 | 4 | 1026 | 236 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-14 | 2.27 | 7.3 | 7.1 | N/S | N/S | N/S | <4 | <4 | 962 | 248 | 4.876 | 2.415 | 19.297 | 2.862 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-15 | 2.07 | 7.4 | 7 | 5 | 2 | <5 | 4 | <4 | 1008 | 262 | 12.031 | 1.934 | 20.747 | 2.85 | <0.005 | <5 | 226.323 | 0.879 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-09-16 | 2.11 | 7.4 | 7.5 | 4 | 3 | N/S | <4 | <4 | 1070 | 308 | <4.000 | 2.22 | 21.913 | 2.237 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.005 | 0.06 | 0.03 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-09-17 | 1.9 | 7.4 | 7.5 | 5 | 2 | N/S | 4 | 4 | 1126 | 326 | <4.000 | 2.193 | 23.201 | 3.129 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-18 | 1.96 | 7.5 | 7.2 | 4 | 3 | N/S | 5 | 5 | 894 | 130 | 4.051 | 2.436 | 21.376 | 3.416 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-19 | 1.92 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 996 | 132 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-20 | 1.98 | 7.5 | 7.1 | N/S | N/S | N/S | 7 | 6 | 1210 | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-21 | 1.79 | 7.5 | 6.5 | N/S | N/S | N/S | 7 | 6 | 1284 | 196 | 6.962 | 3.173 | 17.82 | 2.889 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-22 | 1.94 | 7.4 | 6.9 | 8 | 4 | <5 | 9 | 7 | 1334 | 322 | 4.091 | 4.26 | 18.61 | 3.155 | <0.005 | <5 | 368.854 | 0.966 | 270000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-09-23 | 1.97 | 7.4 | 6.7 | 5 | 3 | N/S | 6 | 5 | 1268 | 282 | 3.713 | 3.792 | 17.793 | 3.089 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.007 | 0.1 | 0.04 | <0.002 | 0.036 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2025-09-24 | 2.01 | 7.4 | 7.2 | 6 | 3 | N/S | 4 | <4 | 1252 | 310 | 1.893 | 2.707 | 18.517 | 3.357 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-25 | 2.02 | 7.4 | 7.3 | 11 | 5 | N/S | 13 | 12 | 1348 | 208 | <4.000 | 3.745 | 20.682 | 3.434 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-26 | 2.23 | 7.4 | 7.2 | N/S | N/S | N/S | 6 | 6 | 1402 | 406 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-27 | 2.06 | 7.4 | 6.8 | N/S | N/S | N/S | 5 | 5 | 1488 | 296 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-28 | 1.88 | 7.3 | 7.1 | N/S | N/S | N/S | 5 | 5 | 1378 | 294 | 2.885 | 3.58 | 18.857 | 3.151 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-09-29 | 1.95 | 7.2 | 7.1 | 10 | 3 | <5 | <4 | <4 | 1364 | 268 | 2.286 | 3.617 | 16.628 | 3.161 | <0.005 | <5 | 409.928 | 0.934 | 2400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-09-30 | 1.96 | 7.4 | 7.1 | 7 | 4 | N/S | <4 | <4 | 1446 | 290 | 3.68 | 3.961 | 15.485 | 2.85 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.006 | 0.09 | 0.04 | <0.002 | 0.017 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.5 | N/S
2025-10-01 | 1.95 | 7.4 | 7.1 | 4 | 2 | N/S | 4 | <4 | 1438 | 296 | T/X | 3.93 | 17.449 | 2.948 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-02 | 1.92 | 7.4 | 7.4 | 5 | 2 | N/S | <4 | <4 | 1422 | 332 | T/X | 4.013 | 19.872 | 3.039 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-03 | 1.92 | 7.4 | 7.1 | N/S | N/S | N/S | <4 | <4 | 1302 | 230 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-04 | 1.86 | 7.5 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1488 | 250 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-05 | 1.89 | 7.4 | 7.1 | N/S | N/S | N/S | <4 | <4 | 1568 | 182 | T/X | 3.543 | 17.582 | 3.047 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-06 | 1.89 | 7.5 | 7.5 | 6 | 3 | <5 | <4 | <4 | 1428 | 196 | <4.000 | 3.282 | 19.376 | 3.089 | 0.005 | <5 | 532.15 | 1.013 | 4200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-10-07 | 3.06 | 7.4 | 7.6 | 5 | 5 | N/S | <4 | <4 | 1074 | 232 | <4.000 | 0.778 | 17.548 | 2.441 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.029 | <0.002 | <0.004 | 0.004 | 0.04 | 0.03 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.028 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-10-08 | 3.12 | 7.3 | 8.2 | <2 | <2 | N/S | <4 | <4 | 1052 | 254 | <4.000 | <0.300 | 15.993 | 1.909 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-09 | 2.12 | 7.4 | 7.7 | 3 | <2 | N/S | <4 | <4 | 1184 | 292 | <4.000 | 0.314 | 18.285 | 2.569 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-10 | 1.95 | 7.4 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1250 | 282 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-11 | 2.03 | 7.3 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1150 | 236 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-12 | 1.99 | 7.4 | 7.8 | N/S | N/S | N/S | <4 | <4 | 1076 | 170 | <4.000 | <0.300 | 21.207 | 2.984 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-13 | 2.13 | 7.4 | 7.7 | T/X | T/X | <5 | <4 | <4 | 938 | 124 | <4.000 | 1.083 | 20.467 | 2.974 | <0.005 | <5 | 234.244 | 0.943 | 7700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 12
2025-10-14 | 1.85 | 7.4 | 7.6 | T/X | T/X | N/S | 4 | <4 | 984 | 168 | <4.000 | 0.556 | 21.059 | 2.923 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.03 | <0.002 | <0.004 | 0.006 | 0.06 | 0.03 | <0.002 | 0.007 | <0.002 | <0.004 | <0.004 | 0.04 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-10-15 | 1.91 | 7.4 | 8 | 5 | <2 | N/S | <4 | <4 | 916 | 154 | <4.000 | 0.552 | 22.826 | 3.145 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-16 | 1.88 | 7.4 | 7.3 | 6 | 3 | N/S | 4 | <4 | 866 | 134 | <4.000 | 1.294 | 22.482 | 2.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-17 | 2.09 | 7.5 | 7.9 | N/S | N/S | N/S | 5 | 4 | 910 | 174 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-18 | 1.85 | 7.5 | 6.9 | N/S | N/S | N/S | 6 | 5 | 884 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-19 | 3.06 | 7.4 | 7.1 | N/S | N/S | N/S | 19 | 15 | 704 | 146 | 5.375 | 2.057 | 14.279 | 2.452 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-20 | 3.54 | 7.3 | 7 | 26 | 11 | <5 | 24 | 20 | 730 | 156 | 5.313 | 2.407 | 9.926 | 1.962 | <0.005 | 6 | 159.057 | 0.701 | 260000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-10-21 | 2.54 | 7.4 | 6.3 | 19 | 8 | N/S | 12 | 11 | 844 | 170 | 4.569 | 2.957 | 10.75 | 2.068 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.011 | 0.14 | 0.04 | <0.002 | 0.025 | <0.002 | <0.004 | <0.004 | 0.046 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.3 | N/S
2025-10-22 | 1.6 | 7.5 | 7.6 | T/X | T/X | N/S | 11 | 10 | 946 | 182 | 3.643 | 2.475 | 11.295 | 2.655 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-23 | 2.31 | 7.4 | 7.5 | T/X | T/X | N/S | 8 | 7 | 1028 | 174 | 2.607 | 3.556 | 14.882 | 2.457 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-24 | 2.05 | 7.5 | 7.6 | N/S | N/S | N/S | 8 | 5 | 1156 | 166 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-25 | 1.91 | 7.4 | 7.6 | N/S | N/S | N/S | 5 | 5 | 1278 | 162 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-26 | 2.05 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1340 | 186 | <4.000 | 2.911 | 19.117 | 3.294 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-27 | 1.97 | 7.4 | 7.4 | 7 | 3 | <5 | 4 | <4 | 1160 | 176 | <4.000 | 2.926 | 18.688 | 3.302 | <0.005 | <5 | 363.415 | 1.016 | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-10-28 | 1.93 | 7.4 | 7.7 | 7 | 3 | N/S | 4 | <4 | 1108 | 212 | <4.000 | 2.114 | 22.695 | 3.343 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.008 | 0.08 | 0.03 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.05 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-10-29 | 1.88 | 7.4 | 7.6 | 6 | 3 | N/S | 4 | 4 | 1112 | 196 | <4.000 | 1.575 | 23.109 | 3.199 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-30 | 1.94 | 7.4 | 7.6 | 6 | 3 | N/S | 6 | 4 | 1028 | 178 | <4.000 | 1.421 | 22.45 | 3.197 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-10-31 | 1.94 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1070 | 116 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-01 | 1.93 | 7.5 | 7.4 | N/S | N/S | N/S | <4 | <4 | 1134 | 110 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-02 | 2.05 | 7.5 | 7.3 | N/S | N/S | N/S | <4 | <4 | 960 | 126 | <4.000 | 2.684 | 21.74 | 3.094 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-03 | 1.96 | 7.4 | 7.8 | 6 | 2 | <5 | <4 | <4 | 860 | 68 | <4.000 | 3.069 | 21.426 | 3.022 | <0.005 | <5 | 231.108 | 1.042 | 40000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-11-04 | 1.92 | 7.4 | 7.8 | 5 | 2 | N/S | <4 | <4 | 852 | 100 | <4.000 | 2.017 | 21.678 | 3.096 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.033 | <0.002 | <0.004 | 0.004 | 0.04 | 0.03 | <0.002 | 0.006 | <0.002 | <0.004 | <0.004 | 0.048 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | <0.5 | N/S
2025-11-05 | 1.94 | 7.4 | 7.9 | T/X | T/X | N/S | 5 | 5 | 940 | 174 | <4.000 | 2.053 | 22.329 | 2.916 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-06 | 1.9 | 7.4 | 7.6 | T/X | T/X | N/S | 4 | <4 | 958 | 172 | <4.000 | 1.963 | 22.017 | 2.983 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-07 | 2 | 7.4 | 7.3 | N/S | N/S | N/S | 5 | 4 | 1004 | 184 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-08 | 1.98 | 7.4 | 7.1 | N/S | N/S | N/S | 4 | 5 | 842 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-09 | 2.44 | 7.3 | 6.2 | N/S | N/S | N/S | 4 | 5 | 792 | 136 | <4.000 | 0.906 | 16.89 | 2.457 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-10 | 3.22 | 7.2 | 7.8 | 12 | 6 | <5 | 6 | 5 | 1024 | 170 | T/X | T/X | T/X | T/X | <0.005 | <5 | 294.613 | 0.913 | 58000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-11-11 | 2.18 | 7.4 | 7.3 | 8 | 4 | N/S | 6 | 6 | 1180 | 146 | 2.894 | 2.69 | 14.853 | 2.308 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.007 | 0.07 | 0.03 | <0.002 | 0.012 | <0.002 | <0.004 | <0.004 | 0.034 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.6 | N/S
2025-11-12 | 2.01 | 7.4 | 7.8 | 7 | 3 | N/S | 4 | 4 | 1058 | 124 | 5.003 | 2.415 | 18.604 | 2.683 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-13 | 1.77 | 7.4 | 7.7 | 6 | <2 | N/S | 6 | 4 | 1030 | 134 | <4.000 | 1.652 | 21.71 | 3.013 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-14 | 1.91 | 7.4 | 7.6 | N/S | N/S | N/S | 7 | 5 | 1032 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-15 | 1.92 | 7.4 | 6.8 | N/S | N/S | N/S | 6 | 4 | 1048 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-16 | 1.95 | 7.5 | 6.9 | N/S | N/S | N/S | 6 | 5 | 1052 | 182 | 4.839 | 4.403 | 20.623 | 3.574 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-17 | 1.94 | 7.4 | 7.7 | 10 | 4 | <5 | 6 | 5 | 988 | 142 | 3.683 | 4.465 | 20.312 | 3.564 | <0.005 | <5 | 230.928 | 1.042 | 66000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-11-18 | 2.29 | 7.4 | 7.4 | 12 | 5 | N/S | 8 | 7 | 946 | 146 | 4.269 | 4.553 | 19.785 | 3.52 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.01 | 0.1 | 0.04 | <0.002 | 0.013 | <0.002 | <0.004 | <0.004 | 0.044 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2025-11-19 | 1.94 | 7.4 | 8.1 | 8 | 3 | N/S | 5 | 4 | 962 | 138 | <4.000 | 2.245 | 22.789 | 3.361 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-20 | 2.01 | 7.4 | 7.5 | 10 | 5 | N/S | 7 | 5 | 946 | 160 | 4.06 | 2.799 | 20.703 | 3.558 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-21 | 1.9 | 7.4 | 7.4 | N/S | N/S | N/S | 4 | <4 | 1042 | 214 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-22 | 1.97 | 7.3 | 7.4 | N/S | N/S | N/S | 8 | 5 | 958 | 196 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-23 | 1.94 | 7.3 | 7.6 | N/S | N/S | N/S | 5 | 4 | 956 | 152 | <4.000 | 1.627 | 20.901 | 3.338 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-24 | 2.17 | 7.3 | 7.7 | T/X | T/X | <5 | 6 | 6 | 984 | 120 | 2.363 | 3.067 | 18.074 | 3.283 | <0.005 | 5 | 238.211 | 1.036 | 4100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11
2025-11-25 | 2.08 | 7.4 | 7.5 | T/X | T/X | N/S | 7 | 5 | 976 | 148 | 3.138 | 2.179 | 14.797 | 2.942 | N/S | N/S | N/S | N/S | N/S | <0.002 | 0.032 | <0.002 | <0.004 | 0.007 | 0.07 | 0.04 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.3 | N/S
2025-11-26 | 2.32 | 7.3 | 8.5 | 9 | 4 | N/S | 6 | 7 | 938 | <50 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-27 | 2.06 | 7.4 | 7.9 | 10 | 5 | N/S | 8 | 7 | 872 | <50 | <4.000 | 1.169 | 17.18 | 2.738 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-28 | 1.93 | 7.4 | 7.9 | N/S | N/S | N/S | <4 | <4 | 990 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-29 | 2.06 | 7.4 | 7.9 | N/S | N/S | N/S | <4 | <4 | 1094 | 222 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-11-30 | 2.17 | 7.4 | 7.7 | N/S | N/S | N/S | <4 | <4 | 1516 | 138 | 1.85 | 1.657 | 17.869 | 2.808 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-01 | 2.35 | 7.3 | 8 | 6 | 3 | <5 | <4 | <4 | 1722 | 136 | 1.819 | 1.69 | 17.557 | 2.716 | 0.011 | <5 | 698.343 | 0.903 | 8200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-12-02 | 2.24 | 7.3 | 7.9 | 5 | 3 | N/S | <4 | <4 | 1938 | 166 | <4.000 | 1.176 | 17.885 | 2.707 | N/S | N/S | 825.991 | N/S | N/S | <0.002 | 0.053 | <0.002 | <0.004 | 0.005 | 0.08 | 0.05 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.036 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.2 | N/S
2025-12-03 | 2.21 | 7.2 | 8.5 | 5 | 4 | N/S | <4 | <4 | 1896 | 174 | <4.000 | 0.857 | 18.267 | 2.611 | N/S | N/S | 798.201 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-04 | 2.16 | 7.3 | 8.2 | 10 | 6 | N/S | 6 | 5 | 1666 | 134 | <4.000 | 0.672 | 18.771 | 2.705 | N/S | N/S | 668.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-05 | 2.06 | 7.4 | 8.2 | N/S | N/S | N/S | 8 | 6 | 1420 | 122 | N/S | N/S | N/S | N/S | N/S | N/S | 531.129 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-06 | 2.12 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 5 | 1284 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 449.798 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-07 | 2.17 | 7.3 | 8.1 | N/S | N/S | N/S | <4 | 4 | 1370 | 180 | <4.000 | 1.17 | 18.884 | 2.807 | N/S | N/S | 491.096 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-08 | 2.26 | 7.3 | 8 | 8 | 5 | <5 | <4 | 4 | 1472 | 126 | 2.403 | 1.401 | 18.3 | 2.742 | 0.008 | <5 | 545.985 | 0.921 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9
2025-12-09 | 2.12 | 7.4 | 8.1 | 6 | 5 | N/S | 4 | 4 | 1392 | 126 | <4.000 | 0.874 | 20.315 | 2.517 | N/S | N/S | 501.609 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.007 | 0.07 | 0.05 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.9 | N/S
2025-12-10 | 3.23 | 7.3 | 8.3 | T/X | T/X | N/S | 8 | 6 | 1716 | 164 | 1.947 | 0.706 | 15.281 | 1.961 | N/S | N/S | 725.525 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-11 | 3.55 | 7.2 | 8.2 | T/X | T/X | N/S | 5 | 4 | 2004 | 254 | 3.289 | 1.277 | 11.608 | 1.661 | N/S | N/S | 838.713 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-12 | 2.35 | 7.4 | 7.4 | N/S | N/S | N/S | 4 | <4 | 1786 | 210 | N/S | N/S | N/S | N/S | N/S | N/S | 700.524 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-13 | 2.35 | 7.4 | 8.4 | N/S | N/S | N/S | 7 | 6 | 1682 | 230 | N/S | N/S | N/S | N/S | N/S | N/S | 636.557 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-14 | 2.35 | 7.4 | 9 | N/S | N/S | N/S | 4 | 4 | 1510 | 156 | <4.000 | 0.668 | 18.247 | 2.297 | N/S | N/S | 562.585 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-15 | 2.24 | 7.4 | 8.6 | 7 | 3 | <5 | 4 | 4 | 1414 | 168 | <4.000 | 0.751 | 19.148 | 2.54 | 0.006 | <5 | 487.325 | 0.928 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10
2025-12-16 | 2.2 | 7.3 | 8.7 | 4 | 3 | N/S | 5 | <4 | 1574 | 214 | <4.000 | 0.643 | 20.696 | 2.668 | N/S | N/S | 552.344 | N/S | N/S | <0.002 | 0.054 | <0.002 | <0.004 | 0.006 | 0.06 | 0.04 | <0.002 | 0.009 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2025-12-17 | 2.19 | 7.3 | 8.5 | 7 | 4 | N/S | 8 | 8 | 1446 | 142 | <4.000 | 0.616 | 19.897 | 2.922 | N/S | N/S | 502.133 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-18 | 2.92 | 7.3 | 8.1 | 9 | 5 | N/S | 12 | 9 | 1262 | 110 | <4.000 | 0.594 | 15.682 | 2.607 | N/S | N/S | 429.813 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-19 | 3.75 | 7.2 | 8.8 | N/S | N/S | N/S | 10 | 8 | 1444 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | 541.172 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-20 | 3.11 | 7.2 | 7.7 | N/S | N/S | N/S | 14 | 11 | 1508 | 220 | N/S | N/S | N/S | N/S | N/S | N/S | 536.432 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-21 | 2.22 | 7.3 | 8.2 | N/S | N/S | N/S | 14 | 12 | 1388 | 184 | 4.131 | 2.568 | 11.653 | 2.368 | N/S | N/S | 460.163 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-22 | 2.32 | 7.3 | 8 | 15 | 8 | <5 | 6 | 5 | 1430 | 168 | 5.892 | 3.471 | 10.698 | 2.578 | 0.006 | <5 | 497.873 | 0.876 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 13
2025-12-23 | 2.19 | 7.3 | 7.9 | 15 | 10 | N/S | 13 | 11 | 1434 | 198 | 5.735 | 3.427 | 11.006 | 2.832 | N/S | N/S | 470.386 | N/S | N/S | <0.002 | 0.048 | <0.002 | <0.004 | 0.01 | 0.11 | 0.05 | <0.002 | 0.024 | <0.002 | <0.004 | <0.004 | 0.043 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2025-12-24 | 3.32 | 7.3 | 7.8 | 15 | 9 | N/S | 14 | 12 | 1226 | 116 | T/X | T/X | T/X | T/X | N/S | N/S | 386.417 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-25 | 2.35 | 7.4 | 7.5 | 16 | 8 | N/S | 7 | 5 | 1266 | 148 | 4.875 | 3.186 | 12.075 | 2.784 | N/S | N/S | 407.336 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-26 | 2.23 | 7.2 | 7.6 | N/S | N/S | N/S | 22 | 17 | 1232 | 144 | N/S | N/S | N/S | N/S | N/S | N/S | 405.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-27 | 2.22 | 7.4 | 7.2 | N/S | N/S | N/S | 8 | 7 | 1176 | 146 | N/S | N/S | N/S | N/S | N/S | N/S | 377.029 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-28 | 3.49 | 7.4 | 7.2 | N/S | N/S | N/S | 19 | 16 | 964 | 146 | 2.755 | 0.589 | 10.556 | 2.044 | N/S | N/S | 317.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2025-12-29 | 4.09 | 7.1 | 8.1 | 9 | 7 | <5 | 17 | 14 | 952 | 144 | 1.79 | <0.300 | 9.033 | 1.093 | 0.008 | <5 | 318.545 | 0.525 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8
2025-12-30 | 3.85 | 7.1 | 8.3 | 9 | 8 | N/S | 10 | 8 | 1156 | 132 | 1.039 | <0.300 | 9.271 | 1.145 | N/S | N/S | 406.74 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.008 | 0.13 | T/X | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.026 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 2.9 | N/S
2025-12-31 | 3.84 | 7.1 | 8.3 | T/X | T/X | N/S | 9 | 8 | 1320 | 130 | T/X | T/X | T/X | T/X | N/S | N/S | 491.038 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
RL effective 1/1/25 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 25 | 1 | 0.3 | 0.5 | 0.15 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
Observations | 365 | 365 | 365 | 187 | 187 | 51 | 365 | 365 | 365 | 365 | 208 | 250 | 250 | 250 | 52 | 52 | 181 | 53 | 51 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 49 | 49 | 49 | 52 | 49 | 49 | 49 | 49 | 49 | 0 | 0 | 0 | 49 | 52
Minimum | 1.14 | 7 | 6.2 | <2 | <2 | <5 | <4 | <4 | 704 | <50 | <1.000 | <0.300 | 5.04 | 0.76 | <0.005 | <5 | 159.057 | 0.525 | 1400 | <0.002 | 0.029 | <0.002 | <0.004 | 0.003 | 0.04 | 0.02 | <0.002 | 0.003 | <0.002 | <0.004 | <0.004 | 0.019 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | <0.5 | 7
Mean | 2.6141 | 7.3616 | 7.9871 | <8 | <4 | <4 | <5 | <5 | 1180.9863 | <192 | <3.041 | <1.475 | 15.1759 | 2.4022 | <0.004 | <4 | 419.0601 | 0.862 | GM=11773 | <0.001 | 0.039673 | <0.001 | <0.003 | 0.0058611 | 0.0775 | 0.04 | <0.001 | 0.015375 | <0.001 | <0.003 | <0.003 | 0.032796 | <0.001 | <0.001 | <0.001 | <2 |  |  |  | <1.2 | 9.7885
Maximum | 4.43 | 7.5 | 9.8 | 26 | 13 | <5 | 24 | 20 | 2004 | 662 | 12.031 | 7.273 | 23.887 | 3.575 | 0.011 | 6 | 838.713 | 1.042 | 270000 | <0.002 | 0.054 | <0.002 | <0.004 | 0.011 | 0.17 | 0.05 | <0.002 | 0.059 | <0.002 | <0.004 | <0.004 | 0.065 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | 10.5 | 16
%>400=100
January 1, 2, 5-9, 12-16, 20-23, 26-30, 2025, TKN, T/X: Expired reagent used.
January 7, 2025, BOD5, CBOD5, T/X: None of the dilution results met the acceptance criteria for the method.
January 19, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved within holding time.
January 22, 2025, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
February 2-6, 9, 10, 12, 13, 17-20, 23-25, 27, 2025, TKN, T/X: Expired reagent used.
February 10, 2025, Phenol: Sample MS/MSD recovery failed but LCS passed.
February 11, 2025, BOD5, CBOD5, T/X: Tests cancelled due to holiday.
February 11, 16, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved within holding time.
February 11, 18, 25, 2025, As, Ba, Cd, Cr-Tot, Pb, Mn, Ni, Se, Zn, Sb, Be, Tl, T/X: Laboratory error, reporting limit requirements were not met.
February 12, 18, 25, 2025, Fe-Sol, T/X: Laboratory error, reporting limit requirements were not met.
February 23, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
March 4, 2025, As, Ba, Cd, Cr, Cu, Fe, Pb, Mn, Ni, Se, Ag, Zn, Sb, Be, Tl: Sample MS/MSD recovery failed but LCS passed.
March 17, 2025, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
March 19, 20, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
March 19, 26, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
March 24, 2025, FOG, T/X: LCS failure.
March 31, 2025, Cr6+, T/X: LCS failure.
April 1, 2025, Fe-S: Sample MS/MSD recovery failed but LCS passed.
April 2, 15, 23, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
April 16, 17, 2025, BOD5, CBOD5, T/X: Method blank failure.
April 21, 2025, Cr6+, T/X: LCS failure.
April 24, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
April 27, 2025, TKN, NH3-N, P-TOT: Sample MS/MSD recovery failed but LCS passed.
May 11, 14, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
May 25, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved due to holiday.
May 27, 2025, Hg LL, T/X: Field blank failure.
June 1, 5, 29, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
June 2, 2025, Cr6+, T/X: LCS failure.
June 18, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved due to holiday.
June 25, 2025, TKN, P-TOT: Sample MS/MSD recovery failed but LCS passed.
July 1, 2025 Hg LL, T/X: OPR failure.
July 3, 2025, BOD5, CBOD5, T/X: Sample received past 48-hour hold time due to holiday.
July 7, 2025, P-TOT, TKN: MS/MSD recovery failed but LCS passed.
July 8, 2025, P-TOT: MS/MSD recovery failed but LCS passed.
July 22, 29, 2025, Fe-S: MS/MSD recovery failed but LCS passed.
August 3, 11, 14, 25, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
August 20, 2025, TKN, T/X: Innapropriate dilution factor.
August 27, 28, BOD5, CBOD5, T/X: GGA failure.
August 31, 2025, P-TOT, NO2-N+NO3-N, TKN, NH3-N, T/X: Aliquot not preserved within holding time due to holiday.
September 7, 2025, TKN, NO2-N+NO3-N, P-TOT: Sample MS/MSD recovery failed but LCS passed.
September 8, 2025, TKN, P-TOT: Sample MS/MSD recovery failed but LCS passed.
September 9, 2025, Hg LL, T/X: Field blank for sample was greater than the LOQ.
September 11, 16, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
September 17, 2025, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
September 21, 23, 2025, NH3-N: Sample MS/MSD recovery failed but LCS passed.
September 28, 29, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
October 1, 2, 5, 2025, TKN, T/X: Ammonia result greater than TKN.
Ocober 6, 12, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
October 13,14, 2025, BOD5, CBOD5, T/X: None of the dilution results met the acceptance criteria for the method.
October 22, 26, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
October 22, 23, 2025, BOD5, CBOD5, T/X: Method blank failure.
November 2, 11, 13, 16, 17, 20, 30, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
November 5, 6, 2025, BOD5, CBOD5, T/X: Method blank failure.
November 10, 26, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved due to holiday.
November 16, 18, 2025, TKN : Sample MS/MSD recovery failed but LCS passed.
November 24, 25, 2025, BOD5, CBOD5, T/X: None of the dilution results met the acceptance criteria for the method.
December 3, 2025, P-TOT: Sample MS/MSD recovery failed but LCS passed.
December 8, 2025, Phenol: Sample MS/MSD and RPD failed, but LCS passed.
December 10, 30, 2025, TKN: Sample MS/MSD recovery failed but LCS passed.
December 10, 11, 2025, BOD5, CBOD5, T/X: GGA failure.
December 14, 2025, NO2-N+NO3-N: Sample MS/MSD recovery failed but LCS passed.
December 24, 31, 2025, TKN, NH3-N, NO2-N+NO3-N, P-TOT, T/X: Aliquot not preserved due to holiday.
December 30, 2025, Fe-S, T/X: Method blank failure.
December 31, 2025, BOD5, CBOD5, T/X: None of the dilution results met the acceptance criteria for the method.

## Lemont Outfall 2026
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | CFU/100ml | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2026-01-01 | 3.56 | 7.3 | 7.1 | T/X | T/X | N/S | 18 | 16 | 1466 | 136 | 6.057 | 3.422 | T/X | 1.902 | N/S | N/S | 551.361 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-02 | 3.07 | 7 | 7.7 | N/S | N/S | N/S | 29 | 24 | 1350 | 148 | N/S | N/S | N/S | N/S | N/S | N/S | 490.524 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-03 | 2.45 | 7.3 | 7.2 | N/S | N/S | N/S | 11 | 10 | 1302 | 156 | N/S | N/S | N/S | N/S | N/S | N/S | 446.085 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-04 | 2.36 | 7.2 | 7.7 | N/S | N/S | N/S | 9 | 7 | 1210 | 142 | 4.128 | 1.598 | 13.714 | 2.788 | N/S | N/S | 394.163 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-05 | 2.37 | 7.3 | 7.1 | 16 | 10 | <5.00 | 18 | 14 | 1228 | 110 | 5.008 | 3.066 | 11.244 | 2.713 | 0.009 | <5 | 379.862 | 0.902 | 77000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 16.733
2026-01-06 | 2.36 | 7.4 | 7.2 | 15 | 8 | N/S | 9 | 8 | 1236 | 130 | 5.516 | 2.421 | 10.083 | 2.678 | N/S | N/S | 410.518 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.012 | 0.14 | 0.05 | <0.002 | 0.028 | <0.002 | <0.004 | <0.004 | 0.043 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1 | N/S
2026-01-07 | 2.38 | 7.3 | 7.1 | 16 | 9 | N/S | 12 | 10 | 1312 | 126 | 5.073 | 2.367 | 11.826 | 2.613 | N/S | N/S | 457.683 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-08 | 2.35 | 7.4 | 7.2 | 11 | 8 | N/S | 10 | 9 | 1290 | 120 | 3.941 | 1.676 | 11.402 | 2.507 | N/S | N/S | 468.854 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-09 | 3.77 | 7.2 | 8.7 | N/S | N/S | N/S | 57 | 46 | 1032 | 216 | N/S | N/S | N/S | N/S | N/S | N/S | 341.173 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-10 | 3.8 | 7.4 | 8.5 | N/S | N/S | N/S | 6 | 6 | 1090 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 389.817 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-11 | 3.75 | 7.3 | 7.7 | N/S | N/S | N/S | 7 | 6 | 1110 | 144 | 1.728 | 0.432 | 9.668 | 1.061 | N/S | N/S | 383.819 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-12 | 3.7 | 7.2 | 7.5 | 7 | 5 | <5.00 | 5 | 5 | 1040 | 118 | 2.001 | 0.683 | 8.867 | 1.2 | <0.005 | <5 | 343.267 | 0.683 | 46000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9.809
2026-01-13 | 3.81 | 7.3 | 8.4 | 8 | 5 | N/S | 6 | 6 | 1080 | 104 | 1.648 | 0.422 | 9.95 | 1.256 | N/S | N/S | 383.591 | N/S | N/S | <0.002 | 0.041 | <0.002 | <0.004 | 0.007 | 0.11 | 0.05 | <0.002 | 0.008 | <0.002 | <0.004 | <0.004 | 0.027 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 2.1 | N/S
2026-01-14 | 3.77 | 7.3 | 8.5 | 7 | 4 | N/S | 6 | 6 | 1178 | 136 | 1.487 | 0.885 | 11.858 | 1.391 | N/S | N/S | 435.031 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-15 | 3.72 | 7.2 | 8.7 | 7 | 4 | N/S | 6 | 6 | 1164 | 120 | 2.068 | 1.275 | 12.253 | 1.548 | N/S | N/S | 405.822 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-16 | 3.71 | 7.2 | 8.4 | N/S | N/S | N/S | 6 | 4 | 1230 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | 437.137 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-17 | 3.5 | 7.3 | 8.3 | N/S | N/S | N/S | 8 | 5 | 1316 | 108 | N/S | N/S | N/S | N/S | N/S | N/S | 465.112 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-18 | 2.26 | 7.4 | 8.2 | N/S | N/S | N/S | 8 | 6 | 1286 | 138 | T/X | T/X | T/X | T/X | N/S | N/S | 439.803 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-19 | 2.35 | 7.3 | 8.8 | 6 | 4 | <5.00 | 6 | 4 | 1318 | 180 | <4.000 | 2.42 | 13.875 | 2.182 | 0.005 | <5 | 415.065 | 0.953 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 9.457
2026-01-20 | 2.52 | 7.3 | 8.9 | 8 | 5 | N/S | 6 | 5 | 1246 | 108 | <4.000 | 1.56 | 16.63 | 2.174 | N/S | N/S | 450.343 | N/S | 12000 | <0.002 | 0.042 | <0.002 | <0.004 | 0.009 | 0.11 | 0.05 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.032 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 1 | N/S
2026-01-21 | 1.72 | 7.4 | 8.5 | 10 | 5 | N/S | 4 | <4 | 1330 | 216 | <4.000 | 1.081 | 18.442 | 2.484 | N/S | N/S | 428.419 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-22 | 2.82 | 7.3 | 9.4 | 7 | 3 | N/S | <4 | <4 | 1270 | 114 | <4.000 | 2.563 | 16.908 | 2.461 | N/S | N/S | 424.321 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-23 | 2.18 | 7.4 | 9 | N/S | N/S | N/S | <4 | <4 | 1184 | 102 | N/S | N/S | N/S | N/S | N/S | N/S | 404.512 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-24 | 2.24 | 7.4 | 9.4 | N/S | N/S | N/S | 4 | 4 | 1172 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 368.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-25 | 2.17 | 7.4 | 9.3 | N/S | N/S | N/S | 4 | 4 | 1330 | 174 | <4.000 | 0.641 | 19.312 | 2.252 | N/S | N/S | 448.523 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-26 | 2.29 | 7.2 | 8.8 | T/X | T/X | <5.00 | 5 | 4 | 1422 | 178 | <4.000 | 0.936 | 18.098 | 2.317 | <0.005 | <5 | 461.333 | 1.048 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 9.177
2026-01-27 | 2.19 | 7.3 | 9.1 | T/X | T/X | N/S | 4 | 4 | 1410 | 208 | <4.000 | 0.79 | 19.144 | 2.331 | N/S | N/S | 440.095 | N/S | N/S | <0.002 | 0.036 | <0.002 | <0.004 | 0.007 | 0.08 | 0.05 | <0.002 | 0.011 | <0.002 | <0.004 | <0.004 | 0.047 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.4 | N/S
2026-01-28 | 2.13 | 7.3 | 9.2 | 13 | 8 | N/S | 13 | 11 | 1246 | 150 | 4.087 | 1.038 | 19.066 | 2.714 | N/S | N/S | 418.345 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-29 | 2.02 | 7.4 | 9 | 10 | 5 | N/S | 6 | 6 | 1218 | 226 | <4.000 | 0.79 | 20.97 | 2.641 | N/S | N/S | 420.418 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-30 | 2.12 | 7.3 | 8.8 | N/S | N/S | N/S | 5 | 4 | 1224 | 212 | N/S | N/S | N/S | N/S | N/S | N/S | 420.955 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-01-31 | 2.13 | 7.3 | 8.6 | N/S | N/S | N/S | 10 | 9 | 1232 | 118 | N/S | N/S | N/S | N/S | N/S | N/S | 434.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-01 | 2.07 | 7.4 | 6.8 | N/S | N/S | N/S | 7 | 6 | 1246 | 210 | <4.000 | 2.104 | 19.33 | 2.87 | N/S | N/S | 452.389 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-02 | 2.2 | 7.3 | 7.9 | 21 | 9 | <5.00 | 12 | 11 | 1468 | 194 | 3.966 | 2.997 | 16.726 | 2.78 | <0.005 | <5 | 537.262 | 1.086 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 17.452
2026-02-03 | 2 | 7.5 | 8.3 | 12 | 5 | N/S | 11 | 11 | 1490 | 184 | 3.346 | 1.437 | 18.811 | 2.866 | N/S | N/S | 569.725 | N/S | N/S | <0.002 | 0.046 | <0.002 | <0.004 | 0.012 | 0.16 | 0.05 | <0.002 | 0.029 | <0.002 | <0.004 | <0.004 | 0.053 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 1.1 | N/S
2026-02-04 | 2.17 | 7.3 | 8 | 13 | 6 | N/S | 9 | 8 | 1364 | 244 | 2.167 | 1.446 | 18.982 | 2.864 | N/S | N/S | 484.394 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-05 | 1.79 | 7.3 | 8.5 | 23 | 9 | N/S | 21 | 18 | 1514 | 254 | 1.898 | 0.659 | 18.717 | 2.82 | N/S | N/S | 551.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-06 | 2.07 | 7.4 | 8.6 | N/S | N/S | N/S | 18 | 15 | 1440 | 206 | N/S | N/S | N/S | N/S | N/S | N/S | 503.597 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-07 | 2.11 | 7.5 | 8.6 | N/S | N/S | N/S | 11 | 9 | 1282 | 160 | N/S | N/S | N/S | N/S | N/S | N/S | 444.563 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-08 | 2.14 | 7.5 | 8.1 | N/S | N/S | N/S | 8 | 8 | 1336 | 208 | <4.000 | 2.576 | 17.863 | 2.877 | N/S | N/S | 445.204 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-09 | 1.85 | 7.3 | 8.5 | 9 | 5 | <5.00 | 6 | 6 | 1276 | 148 | 4.148 | 1.964 | 18.449 | 2.824 | <0.005 | <5 | 427.32 | 1.133 | 15000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 13.954
2026-02-10 | 2.07 | 7.3 | 8.5 | 10 | 5 | N/S | 4 | <4 | 1230 | 138 | <4.000 | 1.143 | 19.975 | 2.874 | N/S | N/S | 386.05 | N/S | N/S | <0.002 | 0.035 | <0.002 | <0.004 | 0.008 | 0.1 | 0.06 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.058 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
2026-02-11 | 2.27 | 7.4 | 8.7 | 18 | 7 | N/S | 8 | 6 | 1228 | 144 | T/X | T/X | T/X | T/X | N/S | N/S | 373.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-12 | 2.03 | 7.5 | 8.7 | 19 | 7 | N/S | 11 | 9 | 1204 | 140 | 4.222 | 2.089 | 19.574 | 2.883 | N/S | N/S | 370.293 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-13 | 2.01 | 7.4 | 8.3 | N/S | N/S | N/S | 8 | 7 | 1128 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 322.813 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-14 | 1.99 | 7.4 | 7.7 | N/S | N/S | N/S | 12 | 11 | 1182 | 222 | N/S | N/S | N/S | N/S | N/S | N/S | 330.206 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-15 | 2.01 | 7.3 | 7.5 | N/S | N/S | N/S | 8 | 8 | 1148 | 166 | T/X | T/X | T/X | T/X | N/S | N/S | 361.811 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-16 | 2.2 | 7.4 | 7.6 | 16 | 7 | <5.00 | 8 | 7 | 1140 | 226 | 5.134 | 4.088 | 14.102 | 2.569 | <0.005 | <5 | 348.672 | 1.077 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 16.333
2026-02-17 | 2.09 | 7.4 | 8 | 12 | 6 | N/S | 6 | 5 | 1226 | 214 | 4.066 | 2.402 | 14.842 | 2.408 | N/S | N/S | 380.473 | N/S | 330000 | <0.002 | 0.037 | <0.002 | <0.004 | 0.008 | 0.12 | 0.05 | <0.002 | 0.015 | <0.002 | <0.004 | <0.004 | 0.052 | <0.002 | <0.002 | <0.002 | <3 | N/S | N/S | N/S | 1 | N/S
2026-02-18 | 2.02 | 7.3 | 7.9 | 19 | 9 | N/S | 14 | 15 | 1826 | 194 | 4.414 | 1.5 | 16.152 | 2.61 | N/S | N/S | 575.518 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-19 | 2.49 | 7.4 | 8.4 | 12 | 7 | N/S | 4 | 4 | 1730 | 230 | <4.000 | 1.356 | 15.677 | 2.19 | N/S | N/S | 672.737 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-20 | 2.16 | 7.3 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1508 | 142 | N/S | N/S | N/S | N/S | N/S | N/S | 579.211 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-21 | 2.05 | 7.4 | 8.9 | N/S | N/S | N/S | <4 | <4 | 1322 | 158 | N/S | N/S | N/S | N/S | N/S | N/S | 503.349 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-22 | 2.01 | 7.4 | 8.9 | N/S | N/S | N/S | <4 | <4 | 1210 | 144 | 2.865 | 1.514 | 18.444 | 2.965 | N/S | N/S | 413.007 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-23 | 2.1 | 7.3 | 9.3 | 8 | 5 | <5.00 | <4 | <4 | 888 | 104 | <4.000 | 1.847 | 16.402 | 2.759 | 0.005 | <5 | 358.222 | 1.121 | 1300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 14.864
2026-02-24 | 2.02 | 7.4 | 9.2 | 10 | 6 | N/S | <4 | <4 | 1060 | 168 | 2.715 | 1.603 | 17.13 | 2.854 | N/S | N/S | 404.463 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.006 | 0.06 | 0.05 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.9 | N/S
2026-02-25 | 2.05 | 7.3 | 8.5 | T/X | T/X | N/S | 9 | 8 | 1158 | 134 | <4.000 | 1.524 | 18.304 | 3.154 | N/S | N/S | 391.715 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-26 | 2.01 | 7.3 | 9 | T/X | T/X | N/S | <4 | <4 | 1252 | 154 | 1.889 | 1.116 | 17.983 | 2.894 | N/S | N/S | 424.313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-27 | 1.97 | 7.3 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1308 | 194 | N/S | N/S | N/S | N/S | N/S | N/S | 432.606 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-02-28 | 2.07 | 7.3 | 8.1 | N/S | N/S | N/S | <4 | <4 | 1356 | 172 | N/S | N/S | N/S | N/S | N/S | N/S | 460.523 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-01 | 2.07 | 7.2 | 8.5 | N/S | N/S | N/S | <4 | <4 | 1394 | 154 | 4.56 | 3.01 | 13.99 | 2.879 | N/S | N/S | 461.387 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-02 | 1.98 | 7.3 | 8.7 | T/X | T/X | T/X | <4 | <4 | 1334 | 168 | 3.856 | 2.263 | 12.82 | 2.753 | 0.005 | <5 | 447.339 | 1.158 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 14.37
2026-03-03 | 2.07 | 7.3 | 8.7 | T/X | T/X | N/S | 10 | 9 | 1332 | 262 | 2.31 | 1.21 | 15.897 | 2.873 | N/S | N/S | 423.515 | N/S | N/S | <0.002 | 0.044 | <0.002 | <0.004 | 0.008 | 0.1 | 0.04 | <0.002 | 0.016 | <0.002 | <0.004 | <0.004 | 0.035 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.6 | N/S
2026-03-04 | 1.96 | 7.3 | 8.8 | 10 | 8 | N/S | 5 | 4 | 1204 | 142 | <4.000 | 0.938 | 18.882 | 2.854 | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-05 | 2.05 | 7.3 | 8.5 | 11 | 5 | N/S | 6 | 5 | 1192 | 146 | 2.22 | 0.955 | 18.668 | 2.984 | N/S | N/S | 395.246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-06 | 2.4 | 7.3 | 8.5 | N/S | N/S | N/S | 9 | 7 | 1288 | 140 | N/S | N/S | N/S | N/S | N/S | N/S | 459.471 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-07 | 3.86 | 7.2 | 8.3 | N/S | N/S | N/S | 8 | 6 | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | 576.791 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-08 | 3.74 | 7.3 | 8.3 | N/S | N/S | N/S | 55 | 47 | 830 | 158 | 2.268 | 0.713 | 9.807 | 1.277 | N/S | N/S | 581.616 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-09 | 3.53 | 7.1 | 7.9 | 12 | 5 | <5.00 | 8 | 6 | 1408 | 166 | 2.772 | 1.584 | 8.541 | 1.54 | 0.006 | <5 | 518.674 | 0.826 | 5800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 11.55
2026-03-10 | 3.01 | 7.2 | 7.9 | 13 | 6 | N/S | 5 | 5 | 1280 | 132 | 2.132 | 1.15 | 11.933 | 1.791 | N/S | N/S | 471.273 | N/S | N/S | <0.002 | 0.047 | <0.002 | <0.004 | 0.007 | 0.1 | 0.05 | <0.002 | 0.014 | <0.002 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | T/X | N/S
2026-03-11 | 4.03 | 7.2 | 9.4 | 7 | 5 | N/S | 6 | 4 | 1058 | 142 | 1.515 | <0.300 | 9.555 | 1.293 | N/S | N/S | 404.888 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-12 | 4.1 | 7.2 | 9 | 8 | 4 | N/S | 5 | 4 | 1162 | 156 | <4.000 | 0.384 | 10.237 | 1.092 | N/S | N/S | 447.736 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-13 | 4.08 | 7.2 | 8.6 | N/S | N/S | N/S | <4 | <4 | 1274 | 176 | N/S | N/S | N/S | N/S | N/S | N/S | 407.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-14 | 3.91 | 7.2 | 8.4 | N/S | N/S | N/S | <4 | <4 | 1274 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 417.186 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-15 | 3.72 | 7.2 | 8 | N/S | N/S | N/S | <4 | <4 | 1172 | 158 | 2.76 | 1.949 | 8.732 | 1.515 | N/S | N/S | 376.359 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-16 | 4.1 | 7.2 | 9.7 | 3 | <2 | <5.00 | <4 | <4 | 1194 | 178 | 1.455 | <0.300 | 8.087 | 0.858 | <0.005 | <5 | 324.242 | 0.514 | 5200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 8.286
2026-03-17 | 4.09 | 7.3 | 9.8 | 6 | 3 | N/S | 6 | 5 | 1208 | 196 | 1.07 | <0.300 | 9.854 | 0.907 | N/S | N/S | 437.157 | N/S | N/S | <0.002 | 0.04 | <0.002 | <0.004 | 0.008 | 0.11 | 0.03 | <0.002 | 0.009 | 0.003 | <0.004 | <0.004 | 0.031 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | T/X | N/S
2026-03-18 | 4.04 | 7.3 | 9.5 | 3 | <2 | N/S | <4 | <4 | 1206 | 150 | <1.000 | <0.300 | 9.906 | 1.037 | N/S | N/S | 464.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-19 | 4.1 | 7.2 | 9 | 3 | <2 | N/S | <4 | <4 | T/X | T/X | 1.058 | <0.300 | 10.205 | 1.131 | N/S | N/S | 492.822 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-20 | 4.07 | 7.2 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1324 | 276 | N/S | N/S | N/S | N/S | N/S | N/S | 452.169 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-21 | 3.69 | 7.3 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1210 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | 417.498 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-22 | 4.09 | 7.3 | 7.8 | N/S | N/S | N/S | 4 | 4 | 1138 | 162 | 1.867 | 0.51 | 9.964 | 1.453 | N/S | N/S | 401.771 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-23 | 4.05 | 7.2 | 8.6 | 10 | 3 | <5.00 | 6 | 5 | 1144 | 184 | 3.622 | 2.39 | 11.186 | 1.7 | <0.005 | <5 | 384.185 | 0.721 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 10.177
2026-03-24 | 3.69 | 7.2 | 8.6 | 12 | 9 | N/S | <4 | 4 | 1196 | 180 | 5.124 | 3.602 | 9.104 | 2.09 | N/S | N/S | 388.912 | N/S | N/S | <0.002 | 0.043 | <0.002 | <0.004 | 0.006 | 0.11 | 0.07 | <0.002 | 0.036 | <0.002 | <0.004 | <0.004 | 0.033 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.7 | N/S
2026-03-25 | 2.82 | 7.3 | 8.2 | 6 | 4 | N/S | 5 | 4 | 1076 | 74 | 4.502 | 3.523 | 9.84 | 2.375 | N/S | N/S | 383.988 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-26 | 2.72 | 7.3 | 8.3 | 5 | <2 | N/S | <4 | <4 | 1084 | 140 | <4.000 | 0.574 | 14.623 | 2.143 | N/S | N/S | 353.187 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-27 | 3.93 | 7.2 | 9.4 | N/S | N/S | N/S | <4 | <4 | 1144 | 282 | N/S | N/S | N/S | N/S | N/S | N/S | 357.877 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-28 | 3.99 | 7.2 | 8.9 | N/S | N/S | N/S | 4 | <4 | 1050 | 112 | N/S | N/S | N/S | N/S | N/S | N/S | 357.408 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-29 | 3.78 | 7.1 | 8.2 | N/S | N/S | N/S | <4 | <4 | 1114 | 192 | 1.538 | 0.912 | 9.57 | 1.357 | N/S | N/S | 340.521 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2026-03-30 | 3.47 | 7.2 | 8.1 | 9 | 4 | <5.00 | 4 | 4 | 1114 | 166 | 2.354 | 1.606 | 8.919 | 1.61 | <0.005 | <5 | 338.799 | 0.692 | 33000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S | N/S | N/S | N/S | 12.298
2026-03-31 | 3.98 | 7.3 | 9 | 4 | 2 | N/S | <4 | <4 | 844 | 136 | 1.455 | <0.300 | 7.328 | 1.106 | N/S | N/S | 273.045 | N/S | N/S | <0.002 | 0.034 | <0.002 | <0.004 | 0.005 | 0.07 | 0.04 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | N/S | N/S | N/S | N/S | 0.8 | N/S
RL Effective 1/1/2026 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 | 25 | 1 | 0.3 | 0.5 | 0.25 | 0.005 | 5 | 0.5 | 0.1 |  | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 0.5 | 0.5 |  | 0.5 | 5
RL Effective 3/1/2026 | [13 empty] | 0.15
Observations | 90 | 90 | 90 | 44 | 44 | 12 | 90 | 90 | 88 | 88 | 61 | 61 | 60 | 61 | 13 | 13 | 89 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 0 | 0 | 0 | 11 | 13
Minimum | 1.72 | 7 | 6.8 | 3 | <2 | <5.00 | <4 | <4 | 830 | 74 | <1.000 | <0.300 | 7.328 | 0.858 | <0.005 | <5 | 273.045 | 0.514 | 1200 | <0.002 | 0.034 | <0.002 | <0.004 | 0.005 | 0.06 | 0.03 | <0.002 | 0.004 | <0.002 | <0.004 | <0.004 | 0.021 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | 0.6 | 8.286
Mean | 2.7857 | 7.2989 | 8.4233 | 10.5682 | <5 | <4.00 | <8 | <7 | 1241.9318 | 163.4545 | <2.964 | <1.508 | 14.1404 | 2.195 | <0.005 | <4 | 429.448 | 0.91646 | 13532 | <0.001 | 0.040846 | <0.001 | <0.003 | 0.0079231 | 0.10538 | 0.049231 | <0.001 | 0.016769 | <0.001 | <0.003 | <0.003 | 0.038154 | <0.001 | <0.001 | <0.001 | <2 |  |  |  | 1.0364 | 12.6508
Maximum | 4.1 | 7.5 | 9.8 | 23 | 10 | <5.00 | 57 | 47 | 1826 | 282 | 6.057 | 4.088 | 20.97 | 3.154 | 0.009 | <5 | 672.737 | 1.158 | 330000 | <0.002 | 0.047 | <0.002 | <0.004 | 0.012 | 0.16 | 0.07 | <0.002 | 0.036 | 0.003 | <0.004 | <0.004 | 0.058 | <0.002 | <0.002 | <0.002 | <3 |  |  |  | 2.1 | 17.452
%>400=100
January 1, 2026, BOD5, CBOD5, T/X: None of the dilution results met the acceptance criteria for the method.
January 1, 2026, NO2-N + NO3-N, T/X: Analytical error; expired reagents.
January 5-6, 29, 2026, TP: Sample MS/MSD recovery failed but LCS passed.
January 18, 2026, TKN, NH3, NO2-N + NO3-N, P-TOT, T/X: Improper sample preservation.
January 20, 22, 2026, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
January 25-26, 2026, BOD5, CBOD5, T/X: LCS failure.
February 3, 26, 2026, TKN: Sample MS/MSD recovery failed but LCS passed.
February 5, 25-26, 2026, TP: Sample MS/MSD recovery failed but LCS passed.
February 9, 2026, NO2+NO3: Sample MS/MSD recovery failed but LCS passed.
February 11, 15, 2026, TKN, NH3, NO2-N + NO3-N, P-TOT, T/X: Improper sample preservation.
February 25-26, 2026, BOD5, CBOD5, T/X: LCS failure.
March 1, 19, 2026, TKN: Sample MS/MSD recovery failed but LCS passed.
March 2, 2026, FOG: T/X: LCS failure.
March 2-3, 2026, BOD5, CBOD5, T/X: LCS failure.
March 4, 2026, CL, T/X: Duplicate failure.
March 7, 2026, TS, VTS, T/X: Method blank failure.
March 12, 2026, CL: Sample MS/MSD recovery failed but LCS passed.
March 19, 2026, TS, VTS, T/X: LCS failure.
March 31, 2026, Ag: Sample MS/MSD recovery failed but LCS passed.