## Egan Raw 2021
| pH | BOD5 | CBOD5 | TS | SS | TKN | NH3-N | NO2+NO3 | P-TOT | P-SOL | Cl | F | FOG | Phenol-Man | CN (GRAB) | WAD CN | As | Ba | Cd | Cr_Tot | Cu | Fe_Tot | Fe_Sol | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr_+6 | TOC
Date |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | MG/L | mg/L | mg/L | mg/L | ug/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L
2021-01-01 | 7.2 | N/S | N/S | 858 | 183 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-02 | 7.4 | N/S | N/S | 992 | 121 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-03 | 7.3 | 208 | N/S | 1211 | 225 | N/S | 15.5 | 1.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 101
2021-01-04 | 7.3 | 148 | N/S | 922 | 154 | N/S | T/X | T/X | N/S | N/S | 277.58 | 0.5 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 85
2021-01-05 | 7.3 | N/S | N/S | 1032 | 232 | 28 | 15.6 | 2.48 | 5.98 | N/S | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.054 | <0.002 | <0.004 | 0.07 | 0.92 | 0.16 | <0.002 | 0.074 | N/S | 0.012 | <0.004 | <0.004 | 0.108 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-01-06 | 7.4 | N/S | N/S | 892 | 198 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-07 | 7.3 | N/S | N/S | 1004 | 220 | N/S | 15.4 | 3.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-08 | 7.3 | N/S | N/S | 812 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-09 | 7.3 | N/S | N/S | 826 | 186 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-10 | 7.3 | 199 | N/S | 790 | 184 | N/S | 16.6 | 1.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 96
2021-01-11 | 7.3 | 195 | N/S | 954 | 296 | N/S | T/X | T/X | N/S | N/S | 184.1 | 0.6 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 135
2021-01-12 | 7.3 | N/S | N/S | 898 | 204 | 30 | 15.6 | 3.68 | 6.06 | N/S | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.053 | <0.002 | <0.004 | 0.069 | 0.85 | 0.14 | <0.002 | 0.08 | T/X | 0.009 | <0.004 | <0.004 | 0.11 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-01-13 | 7.3 | N/S | N/S | 884 | 183 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-14 | 7.4 | N/S | N/S | 908 | 233 | N/S | 16.6 | 2.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-15 | 7.3 | N/S | N/S | 994 | 288 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-16 | 7.3 | N/S | N/S | 1047 | 254 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-17 | 7.3 | 206 | N/S | 1002 | 210 | N/S | 12.3 | 2.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 62
2021-01-18 | 7.4 | 136 | N/S | 956 | 188 | N/S | T/X | T/X | N/S | N/S | 268.65 | 0.5 | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2021-01-19 | 7.4 | N/S | N/S | 938 | 142 | 24 | 12.5 | 3.36 | 5.17 | N/S | N/S | N/S | N/S | N/S | <0.005 | 0.001 | <0.002 | 0.049 | <0.002 | <0.004 | 0.053 | 0.67 | 0.11 | <0.002 | 0.064 | N/S | 0.008 | <0.004 | <0.004 | 0.077 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-01-20 | 7.5 | N/S | N/S | 906 | 110 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-21 | 7.5 | N/S | N/S | 910 | 116 | N/S | 14.6 | 3.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-22 | 7.4 | N/S | N/S | 898 | 133 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-23 | 7.3 | N/S | N/S | 902 | 137 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-24 | 7.4 | 148 | N/S | 822 | 125 | N/S | 13.9 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 63
2021-01-25 | 7.3 | 149 | N/S | 868 | 171 | N/S | T/X | T/X | N/S | N/S | 186.3 | 0.6 | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 91
2021-01-26 | 7.5 | N/S | N/S | 866 | 129 | 28 | 16.4 | 3.46 | 5.46 | N/S | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.041 | <0.002 | <0.004 | 0.039 | 0.4 | 0.14 | <0.002 | 0.064 | N/S | 0.009 | <0.004 | <0.004 | 0.061 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-01-27 | 7.3 | N/S | N/S | 1038 | 167 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-28 | 7.6 | N/S | N/S | 982 | 179 | N/S | 16.6 | 3.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-29 | 7.4 | N/S | N/S | 814 | 192 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-30 | 7.4 | N/S | N/S | 882 | 154 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-01-31 | 7.3 | 194 | N/S | 944 | 183 | N/S | 15.8 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 95
2021-02-01 | 7.4 | 120 | N/S | 1007 | 156 | N/S | T/X | T/X | N/S | N/S | 288.34 | 0.6 | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 81
2021-02-02 | 7.4 | N/S | N/S | 902 | 160 | 30 | 16.3 | 3.11 | 5.66 | N/S | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.048 | <0.002 | <0.004 | 0.055 | 0.74 | 0.17 | <0.002 | 0.073 | N/S | 0.008 | <0.004 | <0.004 | 0.074 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-02-03 | 7.4 | N/S | N/S | 996 | 186 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-04 | 7.2 | N/S | N/S | 1052 | 238 | N/S | 14.8 | 3.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-05 | 7.4 | N/S | N/S | 1176 | 188 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-06 | 7.3 | N/S | N/S | 1058 | 171 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-07 | 7.3 | 176 | N/S | 1034 | 188 | N/S | 14.9 | 3.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 83
2021-02-08 | 7.3 | 159 | N/S | 972 | 163 | N/S | 15.6 | 2.95 | N/S | N/S | 258.1 | 0.6 | 22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 79
2021-02-09 | 7.3 | N/S | N/S | 948 | 146 | 28 | 15.6 | 3.43 | 5.53 | N/S | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.037 | <0.002 | <0.004 | 0.036 | 0.43 | 0.15 | <0.002 | 0.062 | N/S | 0.015 | <0.004 | <0.004 | 0.065 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-02-10 | 7.3 | N/S | N/S | 946 | 148 | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-11 | 7.3 | N/S | N/S | 976 | 225 | N/S | 18 | 4.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-12 | 7.3 | N/S | N/S | 994 | 208 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-13 | 7.2 | N/S | N/S | 1022 | 240 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-14 | 7.1 | 208 | N/S | 1014 | 234 | N/S | 15.7 | 2.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 107
2021-02-15 | 7.3 | 179 | N/S | 902 | 168 | N/S | 14.3 | 3.74 | N/S | N/S | 235.68 | 0.6 | 12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 79
2021-02-16 | 7.3 | N/S | N/S | 948 | 176 | 31 | 17.6 | 3.2 | 6.82 | N/S | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.045 | <0.002 | <0.004 | 0.061 | 0.68 | 0.15 | <0.002 | 0.074 | N/S | 0.012 | <0.004 | <0.004 | 0.091 | <0.002 | <0.002 | <0.002 | S/X | N/S
2021-02-17 | 7.3 | N/S | N/S | 1246 | 433 | N/S | 17.7 | 1.84 | N/S | N/S | N/S | N/S | N/S | 27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-18 | 7.4 | N/S | N/S | 1341 | 533 | N/S | 27.4 | 1.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <3 | N/S
2021-02-19 | 7.5 | N/S | N/S | 1000 | 162 | N/S | 18.2 | 4.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-20 | 7.5 | N/S | N/S | 952 | 162 | N/S | 15.7 | 4.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-21 | 7.4 | 143 | N/S | 904 | 128 | N/S | 16.7 | 2.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 66
2021-02-22 | 7.4 | 172 | N/S | 1247 | 176 | N/S | 16.1 | 2.09 | N/S | N/S | 435.14 | 0.6 | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 99
2021-02-23 | 7.3 | N/S | N/S | 1574 | 220 | 28 | 12.9 | 2.57 | 6.57 | N/S | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.071 | <0.002 | <0.004 | 0.062 | 0.95 | 0.14 | <0.002 | 0.071 | N/S | 0.011 | <0.004 | <0.004 | 0.116 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-02-24 | 7.4 | N/S | N/S | 1894 | 267 | N/S | 8.9 | 2.39 | N/S | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-25 | 7.5 | N/S | N/S | 1768 | 208 | N/S | 8 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-26 | 7.6 | N/S | N/S | 1619 | 142 | N/S | 8.9 | 2.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-27 | 7.5 | N/S | N/S | 1536 | 150 | N/S | 8.2 | 2.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-02-28 | 7.6 | 175 | N/S | 1464 | 204 | N/S | 6 | 1.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 83
2021-03-01 | 7.6 | 111 | N/S | 1307 | 120 | N/S | 6.5 | 2.18 | N/S | N/S | 476.71 | 0.4 | 17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 45
2021-03-02 | 7.7 | N/S | N/S | 1251 | 92 | 15 | 8.4 | 2.13 | 2.86 | N/S | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.061 | <0.002 | <0.004 | 0.027 | 0.42 | 0.08 | <0.002 | 0.053 | N/S | 0.005 | <0.004 | <0.004 | 0.043 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-03-03 | 7.6 | N/S | N/S | 1200 | 106 | N/S | 8.7 | 2.33 | N/S | N/S | N/S | N/S | N/S | 7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-04 | 7.6 | N/S | N/S | 1127 | 90 | N/S | 8.1 | 2.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-05 | 7.6 | N/S | N/S | 1159 | 112 | N/S | 9.7 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-06 | 7.6 | N/S | N/S | 1117 | 98 | N/S | 9.5 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-07 | 7.6 | 102 | N/S | 1089 | 102 | N/S | 10.6 | 1.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 51
2021-03-08 | 7.6 | 87 | N/S | 1044 | 118 | N/S | 11.2 | 2.28 | N/S | N/S | 335.94 | 0.5 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 43
2021-03-09 | 7.6 | N/S | N/S | 1118 | 196 | 24 | 10.5 | 2.28 | 5.37 | N/S | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.069 | <0.002 | 0.005 | 0.071 | 1.15 | 0.1 | <0.002 | 0.071 | N/S | 0.011 | <0.004 | <0.004 | 0.098 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-03-10 | 7.6 | N/S | N/S | 1021 | 106 | N/S | 10.5 | 2.48 | N/S | N/S | N/S | N/S | N/S | 11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-11 | 7.6 | N/S | N/S | 978 | 104 | N/S | 11.6 | 3.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-12 | 7.6 | N/S | N/S | 1046 | 124 | N/S | 12.6 | 3.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-13 | 7.6 | N/S | N/S | 1032 | 150 | N/S | 11.6 | 3.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-14 | 7.5 | 181 | N/S | 1010 | 158 | N/S | 12.5 | 2.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 82
2021-03-15 | 7.5 | 108 | N/S | 956 | 122 | N/S | 14.1 | 2.39 | N/S | N/S | 272.9 | 0.5 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2021-03-16 | 7.5 | N/S | N/S | 1148 | 140 | 24 | 12.4 | 2.9 | 5.23 | N/S | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.054 | <0.002 | <0.004 | 0.044 | 0.59 | 0.12 | <0.002 | 0.065 | N/S | 0.009 | <0.004 | <0.004 | 0.064 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-03-17 | 7.5 | N/S | N/S | 1041 | 202 | N/S | 12.4 | 2.6 | N/S | N/S | N/S | N/S | N/S | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-18 | 7.6 | N/S | N/S | 1146 | 172 | N/S | 8.5 | 2.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-19 | 7.5 | N/S | N/S | 1254 | 246 | N/S | 9.9 | 2.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-20 | 7.5 | N/S | N/S | 1076 | 108 | N/S | 11.2 | 2.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-21 | 7.5 | T/X | N/S | 1060 | 132 | N/S | 11.7 | 2.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2021-03-22 | 7.5 | T/X | N/S | 1018 | 138 | N/S | 12.3 | 2.43 | N/S | N/S | 288.51 | 0.5 | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2021-03-23 | 7.5 | N/S | N/S | 1066 | 186 | 24 | 12 | 3.14 | 5.32 | N/S | N/S | N/S | N/S | N/S | 0.007 | <0.001 | <0.002 | 0.059 | <0.002 | <0.004 | 0.055 | 0.75 | 0.13 | <0.002 | 0.073 | N/S | 0.012 | <0.004 | <0.004 | 0.079 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-03-24 | 7.5 | 132 | N/S | 1020 | 126 | N/S | 12 | 2.85 | N/S | N/S | N/S | N/S | N/S | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-25 | 7.5 | 172 | N/S | 1138 | 226 | N/S | 11.6 | 3.67 | N/S | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-26 | 7.7 | N/S | N/S | 1045 | 118 | N/S | 11.7 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-27 | 7.5 | N/S | N/S | 978 | 116 | N/S | 12.2 | 3.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-03-28 | 7.5 | 162 | N/S | 980 | 152 | N/S | 13 | 2.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 78
2021-03-29 | 7.5 | 120 | N/S | 948 | 140 | N/S | 13.5 | 2.79 | N/S | N/S | 262.87 | 0.6 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 73
2021-03-30 | 7.5 | N/S | N/S | 924 | 104 | 24 | 13.9 | 3.05 | 5.38 | N/S | N/S | N/S | N/S | N/S | 0.008 | <0.001 | <0.002 | 0.047 | <0.002 | <0.004 | 0.042 | 0.5 | 0.12 | <0.002 | 0.07 | N/S | 0.008 | <0.004 | <0.004 | 0.061 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-03-31 | 7.5 | N/S | N/S | 976 | 114 | N/S | 13.7 | 3.76 | N/S | N/S | N/S | N/S | N/S | 9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-01 | 7.6 | N/S | N/S | 980 | 114 | N/S | 14.1 | 4.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-02 | 7.5 | N/S | N/S | 978 | 152 | N/S | 14.4 | 3.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-03 | 7.6 | N/S | N/S | 962 | 176 | N/S | 14.1 | 3.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-04 | 7.3 | 239 | N/S | 938 | 170 | N/S | 14.9 | 2.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2021-04-05 | 7.4 | 152 | N/S | 1010 | 152 | N/S | 15.7 | 2.82 | N/S | N/S | 220.18 | 0.6 | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 92
2021-04-06 | 7.5 | N/S | N/S | 1014 | 148 | 29 | 17.2 | 2.65 | 5.84 | N/S | N/S | N/S | N/S | N/S | 0.007 | <0.001 | <0.002 | 0.049 | <0.002 | <0.004 | 0.052 | 0.68 | 0.16 | <0.002 | 0.08 | N/S | 0.01 | <0.004 | <0.004 | 0.075 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-04-07 | 7.4 | N/S | N/S | 962 | 178 | N/S | 14.8 | 3.68 | N/S | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-08 | 7.3 | N/S | N/S | 1032 | 275 | N/S | 15.7 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-09 | 7.2 | N/S | N/S | 1527 | 629 | N/S | 16.4 | 1.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-10 | 7.4 | N/S | N/S | 1060 | 254 | N/S | 15.8 | 3.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-11 | 7.5 | 113 | N/S | 962 | 122 | N/S | 13.5 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2021-04-12 | 7.4 | 130 | N/S | 974 | 134 | N/S | 14.7 | 2.86 | N/S | N/S | 246.18 | 0.5 | 9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 82
2021-04-13 | 7.5 | N/S | N/S | 1340 | 454 | 37 | 15.2 | 2.5 | 7.67 | N/S | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.077 | <0.002 | 0.007 | 0.112 | 1.4 | 0.18 | 0.003 | 0.089 | N/S | 0.012 | <0.004 | <0.004 | 0.162 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-04-14 | 7.5 | N/S | N/S | 914 | 112 | N/S | 15.5 | 3.92 | N/S | N/S | N/S | N/S | N/S | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-15 | 7.4 | N/S | N/S | 944 | 120 | N/S | 14.7 | 4.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-16 | 7.5 | N/S | N/S | 900 | 132 | N/S | 14.7 | 4.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-17 | 7.5 | N/S | N/S | 876 | 118 | N/S | 15.6 | 3.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-18 | 7.4 | 147 | N/S | 906 | 128 | N/S | 16.9 | 2.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2021-04-19 | 7.5 | 127 | N/S | 908 | 136 | N/S | 15.2 | 3.87 | N/S | N/S | 203.03 | 0.5 | 42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2021-04-20 | 7.5 | N/S | N/S | 910 | 118 | 27 | 15.4 | 4.77 | 6.01 | N/S | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.041 | <0.002 | <0.004 | 0.043 | 0.62 | 0.16 | <0.002 | 0.073 | N/S | 0.008 | <0.004 | <0.004 | 0.075 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-04-21 | 7.5 | N/S | N/S | 884 | 160 | N/S | 17.2 | 4.37 | N/S | N/S | N/S | N/S | N/S | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-22 | 7.7 | N/S | N/S | 888 | 126 | N/S | 16.9 | 4.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-23 | 7.4 | N/S | N/S | 876 | 154 | N/S | 16.4 | 4.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-24 | 7.4 | N/S | N/S | 888 | 174 | N/S | 17.5 | 3.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-25 | 7.4 | 174 | N/S | 884 | 158 | N/S | 16.8 | 2.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 97
2021-04-26 | 7.4 | 147 | N/S | 858 | 182 | N/S | 18 | 2.14 | N/S | N/S | 181.06 | 0.5 | 41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2021-04-27 | 7.4 | N/S | N/S | 872 | 168 | 28 | 16.2 | 2.44 | 8.01 | N/S | N/S | N/S | N/S | N/S | 0.009 | <0.001 | <0.002 | 0.052 | <0.002 | <0.004 | 0.066 | 0.98 | 0.18 | <0.002 | 0.088 | N/S | 0.008 | <0.004 | <0.004 | 0.099 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-04-28 | 7.4 | N/S | N/S | 994 | 283 | N/S | 18.5 | 1.05 | N/S | N/S | N/S | N/S | N/S | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-29 | 7.5 | N/S | N/S | 912 | 152 | N/S | 17.2 | 3.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-04-30 | 7.5 | N/S | N/S | 860 | 156 | N/S | 17.8 | 2.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-01 | 7.3 | N/S | N/S | 902 | 184 | N/S | 19.1 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-02 | 7.3 | S/X | N/S | S/X | S/X | N/S | S/X | S/X | N/S | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | S/X
2021-05-03 | 7.5 | 151 | N/S | 900 | 192 | N/S | 19.5 | 0.43 | N/S | N/S | 178.82 | 0.5 | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2021-05-04 | 7.5 | N/S | N/S | 900 | 194 | 30 | 16.1 | 3.09 | 6.4 | N/S | N/S | N/S | N/S | N/S | 0.008 | <0.001 | <0.002 | 0.05 | <0.002 | 0.004 | 0.07 | 0.78 | 0.17 | 0.002 | 0.087 | N/S | 0.015 | <0.004 | <0.004 | 0.119 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-05-05 | 7.3 | N/S | N/S | 846 | 154 | N/S | 18.5 | 2.98 | N/S | N/S | N/S | N/S | N/S | 33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-06 | 7.2 | N/S | N/S | 854 | 204 | N/S | 18.8 | 2.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-07 | 7.3 | N/S | N/S | 894 | 176 | N/S | 16.9 | 3.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-08 | 7.3 | N/S | N/S | 968 | 248 | N/S | 17 | 3.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-09 | 7.3 | 268 | N/S | 1056 | 350 | N/S | 15.4 | 2.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 180
2021-05-10 | 7.4 | 116 | N/S | 866 | 162 | N/S | 19.5 | 1.81 | N/S | N/S | 173.48 | 0.5 | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 83
2021-05-11 | 7.3 | N/S | N/S | 784 | 114 | 28 | 17.4 | 3.36 | 6.61 | N/S | N/S | N/S | N/S | N/S | 0.011 | <0.001 | <0.002 | 0.043 | <0.002 | <0.004 | 0.049 | 0.63 | 0.16 | <0.002 | 0.069 | N/S | 0.008 | <0.004 | <0.004 | 0.087 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-05-12 | 7.3 | N/S | N/S | 832 | 146 | N/S | 17 | 3.26 | N/S | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-13 | 7.3 | N/S | N/S | 832 | 170 | N/S | 16.4 | 3.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-14 | 7.3 | N/S | N/S | 884 | 190 | N/S | 15.9 | 3.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-15 | 7.3 | N/S | N/S | 844 | 168 | N/S | 15.1 | 3.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-16 | 7.2 | 146 | N/S | 838 | 172 | N/S | 17 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 80
2021-05-17 | 7.3 | T/X | N/S | 858 | 168 | N/S | 17.3 | 2.18 | N/S | N/S | 159.56 | 0.5 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2021-05-18 | 7.3 | N/S | N/S | 896 | 176 | 31 | 18.4 | 2.16 | 6.77 | N/S | N/S | N/S | N/S | N/S | 0.009 | <0.001 | <0.002 | 0.039 | <0.002 | 0.005 | 0.06 | 0.71 | 0.16 | <0.002 | 0.068 | N/S | 0.009 | <0.004 | <0.004 | 0.101 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-05-19 | 7.3 | N/S | N/S | 800 | 136 | N/S | 16.6 | 3.59 | N/S | N/S | N/S | N/S | N/S | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-20 | 7.3 | N/S | N/S | 872 | 233 | N/S | 16.7 | 4.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-21 | 7.4 | N/S | N/S | 858 | 176 | N/S | 23 | <0.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-22 | 7.2 | N/S | N/S | 834 | 182 | N/S | 15.1 | 2.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-23 | 7.1 | T/X | N/S | 810 | 162 | N/S | 17.7 | <0.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 100
2021-05-24 | 7.1 | 166 | N/S | 860 | 190 | N/S | 18.5 | 1.05 | N/S | N/S | 166.98 | 0.6 | 49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-05-25 | 7.2 | N/S | N/S | 842 | 180 | 32 | T/X | 0.45 | 7.19 | N/S | N/S | N/S | N/S | N/S | 0.017 | <0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.042 | 0.61 | 0.19 | <0.002 | 0.073 | N/S | 0.009 | <0.004 | <0.004 | 0.085 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-05-26 | 7.2 | N/S | N/S | 720 | 279 | N/S | 23.5 | 1.82 | N/S | N/S | N/S | N/S | N/S | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-27 | 7.2 | N/S | N/S | 908 | 228 | N/S | 19.4 | 0.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-28 | 6.9 | N/S | N/S | 968 | 278 | 32 | 15.6 | 2.2 | 8.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-29 | 7.4 | N/S | N/S | 884 | 144 | 25 | 15.5 | 3.11 | 6.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-05-30 | 7.2 | 136 | N/S | 856 | 132 | 29 | 18.1 | 1.42 | 7.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 114
2021-05-31 | 7.2 | 122 | N/S | 872 | 134 | 30 | 19.5 | 4.21 | 6.58 | N/S | 207.01 | 0.6 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 107
2021-06-01 | 7.2 | N/S | N/S | 826 | 122 | 30 | 19.4 | 3.3 | 6.75 | 4.66 | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.039 | <0.002 | <0.004 | 0.053 | 0.68 | 0.2 | <0.002 | 0.069 | N/S | 0.004 | <0.004 | <0.004 | 0.079 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-06-02 | 7.3 | N/S | N/S | 860 | 170 | 35 | 20.5 | <0.25 | 8.83 | N/S | N/S | N/S | N/S | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-03 | 7.2 | N/S | N/S | 864 | 146 | T/X | 18.2 | 1.13 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-04 | 7.2 | N/S | N/S | T/X | T/X | 29 | 17.3 | 1.7 | 8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-05 | 7.1 | N/S | N/S | T/X | T/X | N/S | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-06 | 7.1 | 122 | N/S | 788 | 144 | 27 | 17.7 | 1.25 | 6.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 98
2021-06-07 | 7.2 | 182 | N/S | 858 | 234 | 33 | 18.5 | 1 | 7.41 | N/S | 162.96 | 0.7 | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 120
2021-06-08 | 7.2 | N/S | N/S | 1040 | 384 | 39 | 16.5 | 0.71 | 8.81 | 5.13 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.074 | <0.002 | 0.007 | 0.143 | 1.65 | 0.18 | 0.004 | 0.078 | N/S | 0.022 | <0.004 | <0.004 | 0.232 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-06-09 | 7.3 | N/S | N/S | 884 | 234 | 26 | 16 | 2.46 | 8.42 | N/S | N/S | N/S | N/S | 46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-10 | 7.2 | N/S | N/S | 780 | 134 | 25 | 16.4 | 3.07 | 8.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-11 | 7.2 | N/S | N/S | 782 | 144 | 34 | 23.8 | 1.37 | 7.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-12 | 7.1 | N/S | N/S | 880 | 240 | 34 | 23.3 | 1.11 | 7.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-13 | 7.1 | 144 | N/S | 884 | 178 | 32 | 18.1 | 0.87 | 6.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 110
2021-06-14 | 7.3 | 132 | N/S | 796 | 116 | 17 | 22 | 0.67 | 3.13 | N/S | 172.73 | 0.6 | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 101
2021-06-15 | 7.1 | N/S | N/S | 842 | 128 | 28 | 19.1 | 3.09 | 7.1 | 5.17 | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.047 | <0.002 | <0.004 | 0.061 | 0.88 | 0.19 | <0.002 | 0.076 | N/S | 0.008 | <0.004 | <0.004 | 0.096 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-06-16 | 7.2 | N/S | N/S | 840 | 134 | 32 | 21.8 | 2.33 | 7.91 | N/S | N/S | N/S | N/S | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-17 | 7.4 | N/S | N/S | 796 | 122 | 35 | 23 | 2.49 | 8.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-18 | 7.2 | N/S | N/S | 1311 | 650 | 56 | 23.7 | 0.58 | 11.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-19 | 7.3 | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-20 | 7.3 | 277 | N/S | 932 | 262 | 42 | 24.4 | 1.3 | 7.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 161
2021-06-21 | 7.2 | 372 | N/S | 1151 | 438 | 31 | 12.3 | 1.21 | 6.16 | N/S | 180.32 | 0.4 | 61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 180
2021-06-22 | 7.4 | N/S | N/S | 1473 | 721 | 45 | 19 | <0.25 | 9.68 | 3.59 | N/S | N/S | N/S | N/S | <0.025 | <0.005 | 0.002 | 0.135 | <0.002 | 0.015 | 0.288 | 4.17 | 0.2 | 0.01 | 0.113 | N/S | 0.017 | <0.004 | <0.004 | 0.436 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-06-23 | 7.4 | N/S | N/S | 892 | 80 | 24 | 17.4 | 2.1 | 6.13 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-24 | 7.4 | N/S | N/S | 900 | 204 | 34 | 20.4 | 1.19 | 7.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-25 | 7.4 | N/S | N/S | 864 | 270 | 24 | 10.7 | 0.56 | 4.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-26 | 7.6 | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-06-27 | 7.5 | 90 | N/S | 884 | 106 | 19 | 10.5 | 0.81 | 2.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 65
2021-06-28 | 7.6 | 101 | N/S | 954 | 126 | 22 | 13.1 | <0.25 | 3.69 | N/S | 182.44 | 0.5 | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2021-06-29 | 7.7 | N/S | N/S | 878 | 104 | 21 | 12.8 | 0.91 | 2.88 | 1.12 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.047 | <0.002 | <0.004 | 0.034 | 0.75 | 0.16 | <0.002 | 0.05 | N/S | 0.006 | <0.004 | <0.004 | 0.056 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-06-30 | 7.6 | N/S | N/S | 846 | 132 | 25 | 15 | <0.25 | 4.74 | N/S | N/S | N/S | N/S | 10 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-01 | 7.5 | N/S | N/S | 862 | 98 | 25 | 17 | <0.25 | 4.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-02 | 7.4 | N/S | N/S | 824 | 96 | 24 | 16 | 0.6 | 4.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-03 | 7.4 | N/S | N/S | 850 | 98 | 23 | 17.8 | 1.28 | 4.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-04 | 7.3 | 121 | N/S | 836 | 118 | 28 | 18.8 | <0.25 | 5.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 67
2021-07-05 | 7.4 | 97 | N/S | 844 | 94 | 26 | 18 | 1.77 | 5.72 | N/S | 192.8 | 0.5 | 27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 66
2021-07-06 | 7.4 | N/S | N/S | 804 | 94 | 31 | 22.5 | 0.26 | 6.05 | 4.11 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.044 | <0.002 | <0.004 | 0.045 | 0.75 | 0.21 | <0.002 | 0.075 | N/S | 0.007 | <0.004 | <0.004 | 0.069 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-07-07 | 7.3 | N/S | N/S | 882 | 168 | 35 | 22.5 | 0.81 | 7.54 | N/S | N/S | N/S | N/S | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-08 | 7.3 | N/S | N/S | 950 | 160 | 35 | 22.6 | 0.45 | 7.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-09 | 7.4 | N/S | N/S | 772 | 120 | 26 | 18 | 3.85 | 6.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-10 | 7.2 | N/S | N/S | 880 | 196 | 31 | 24.6 | <0.25 | 5.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-11 | 7.4 | 233 | N/S | 964 | 262 | 37 | 22.4 | <0.25 | 7.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 140
2021-07-12 | 7.5 | 135 | N/S | 832 | 124 | 33 | 23.8 | 0.74 | 5.57 | N/S | 167.04 | 0.7 | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 93
2021-07-13 | 7.2 | N/S | N/S | 948 | 214 | 33 | 19.7 | 1.64 | 7.31 | 4.56 | N/S | N/S | N/S | N/S | 0.008 | <0.001 | <0.002 | 0.056 | <0.002 | <0.004 | 0.068 | 1.07 | 0.23 | <0.002 | 0.082 | N/S | 0.007 | 0.004 | <0.004 | 0.114 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-07-14 | 7.3 | N/S | N/S | 942 | 212 | 36 | 22.9 | <0.25 | 7.79 | N/S | N/S | N/S | N/S | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-15 | 7.4 | N/S | N/S | 820 | 136 | 32 | 21.9 | 0.68 | 6.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-16 | 7.3 | N/S | N/S | 1057 | 387 | 19 | 21.7 | 0.44 | 4.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-17 | 7.4 | N/S | N/S | 788 | 102 | 27 | 22.5 | <0.25 | 4.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-18 | 7.4 | 125 | N/S | 774 | 106 | 30 | 22.7 | 1.12 | 5.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 81
2021-07-19 | 7.4 | 125 | N/S | 804 | 106 | 34 | 24.5 | 0.34 | 5.93 | N/S | 163.92 | 0.6 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 97
2021-07-20 | 7.3 | N/S | N/S | 794 | 92 | 27 | 21.4 | 2.37 | 6.7 | 4.45 | N/S | N/S | N/S | N/S | 0.007 | <0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.048 | 0.78 | 0.2 | <0.002 | 0.062 | N/S | 0.006 | <0.004 | <0.004 | 0.079 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-07-21 | 7.3 | N/S | N/S | 832 | 110 | 30 | 21 | 2.8 | 6.56 | N/S | N/S | N/S | N/S | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-22 | 7.2 | N/S | N/S | 768 | 130 | 34 | 25.4 | 0.78 | 7.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-23 | 7.2 | N/S | N/S | 754 | 144 | 35 | 25.1 | <0.25 | 6.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-24 | 7.2 | N/S | N/S | 808 | 174 | 34 | 25.2 | 0.36 | 6.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-25 | 7.3 | 133 | N/S | 726 | 126 | 26 | 17.8 | 1.03 | 5.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2021-07-26 | 7.1 | 143 | N/S | 800 | 122 | 32 | 24.2 | <0.25 | 6.23 | N/S | 150.83 | 0.7 | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-07-27 | 6.6 | N/S | N/S | 982 | 312 | 38 | 22.9 | <0.25 | 8.4 | 5.08 | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.074 | <0.002 | 0.008 | 0.129 | 1.86 | 0.31 | 0.004 | 0.09 | N/S | 0.012 | <0.004 | <0.004 | 0.223 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-07-28 | 7 | N/S | N/S | 1014 | 367 | 35 | 18.6 | 0.51 | 7.19 | N/S | N/S | N/S | N/S | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-29 | 7.5 | N/S | N/S | 830 | 206 | T/X | 17 | <0.25 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-30 | 7.4 | N/S | N/S | T/X | T/X | 28 | 19.2 | <0.25 | 4.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-07-31 | 7.4 | N/S | N/S | 782 | 116 | 23 | 20.5 | 1.19 | 5.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-08-01 | 7.3 | 221 | 117 | 820 | 168 | 31 | 21 | 1 | 6.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-08-02 | 7.4 | 237 | 126 | 818 | 168 | 32 | 19.7 | 3.2 | 6.16 | N/S | 150.18 | 0.6 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 113
2021-08-03 | 7.2 | 441 | 252 | 944 | 298 | 38 | 23.5 | 1.24 | 7.46 | 4.34 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.054 | <0.002 | 0.006 | 0.088 | 1.31 | 0.25 | 0.003 | 0.085 | N/S | 0.01 | <0.004 | <0.004 | 0.145 | <0.002 | <0.002 | <0.002 | <3 | 168
2021-08-04 | 7.3 | 270 | 112 | 852 | 220 | 26 | 22 | 1.63 | 6.14 | N/S | N/S | N/S | N/S | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 122
2021-08-05 | 7.4 | 290 | N/S | 990 | 302 | 42 | 25.9 | <0.25 | 7.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 128
2021-08-06 | 7.4 | 201 | N/S | 918 | 272 | 38 | 25 | 0.31 | 7.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 101
2021-08-07 | 7.4 | 210 | N/S | 876 | 240 | T/X | 21 | 2.26 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 104
2021-08-08 | 7.3 | 230 | N/S | 794 | 192 | T/X | 22.3 | 1.68 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 111
2021-08-09 | 7.3 | 312 | N/S | 1020 | 350 | 36 | 17.8 | 1.27 | 6.79 | N/S | 142.72 | 0.6 | 70 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 134
2021-08-10 | 7.6 | 86 | N/S | 744 | 118 | T/X | 12.4 | 1.29 | T/X | T/X | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.048 | <0.002 | <0.004 | 0.046 | 0.87 | 0.13 | <0.002 | 0.059 | N/S | 0.005 | <0.004 | <0.004 | 0.083 | <0.002 | <0.002 | <0.002 | <3 | 59
2021-08-11 | 7.5 | T/X | T/X | 734 | 136 | T/X | 10.9 | 1.42 | T/X | N/S | N/S | N/S | N/S | 6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-12 | 7.5 | T/X | T/X | 1000 | 346 | T/X | 16.4 | 0.93 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-13 | 7.4 | T/X | T/X | 910 | 221 | 33 | T/X | T/X | 6.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-14 | 7.4 | 158 | N/S | 776 | 118 | 28 | 19.1 | 1.09 | 5.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2021-08-15 | 7.3 | 176 | N/S | 782 | 138 | 25 | 17 | 3.58 | 5.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 94
2021-08-16 | 7.1 | 223 | N/S | 908 | 236 | 35 | 21.5 | 1.3 | 6.29 | N/S | 159.31 | 0.6 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-08-17 | 7.4 | T/X | T/X | 822 | 179 | 34 | 23.3 | 0.76 | 5.73 | 3.33 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.051 | <0.002 | <0.004 | 0.067 | 1.01 | 0.19 | <0.002 | 0.078 | N/S | 0.006 | <0.004 | <0.004 | 0.112 | <0.002 | <0.002 | <0.002 | <3 | T/X
2021-08-18 | 7.3 | T/X | T/X | 900 | 221 | 35 | 23.7 | 0.71 | 6.33 | N/S | N/S | N/S | N/S | 41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-19 | 7.2 | T/X | T/X | 936 | 287 | 36 | 22.9 | 0.99 | 7.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-20 | 7.3 | T/X | T/X | 850 | 187 | 31 | 22 | 0.99 | 6.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-21 | 7.4 | T/X | T/X | 864 | 158 | 27 | 21 | 2.93 | 5.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-22 | 7.3 | 255 | 137 | 842 | 175 | 37 | 26.5 | <0.25 | 6.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 118
2021-08-23 | 7.1 | 367 | 206 | 954 | 346 | 38 | 23.7 | <0.25 | 7.41 | N/S | 143.31 | 0.6 | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 149
2021-08-24 | 7.3 | T/X | T/X | 884 | 208 | 39 | 22 | <0.25 | 7.65 | 4 | N/S | N/S | N/S | N/S | 0.009 | <0.001 | <0.002 | 0.045 | <0.002 | <0.004 | 0.06 | 0.96 | 0.18 | 0.004 | 0.081 | N/S | 0.013 | <0.004 | <0.004 | 0.11 | 0.002 | <0.002 | <0.002 | <3 | T/X
2021-08-25 | 7.3 | T/X | T/X | 846 | 217 | 30 | 18.6 | 0.55 | 5.66 | N/S | N/S | N/S | N/S | 22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-26 | 7.5 | T/X | T/X | 672 | 136 | 22 | 15.2 | 0.5 | 4.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-27 | 7.2 | T/X | T/X | 728 | 138 | 21 | 18.1 | 0.92 | 4.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-28 | 7.4 | T/X | T/X | 728 | 150 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2021-08-29 | 7.3 | 197 | 103 | 782 | 246 | 30 | 16.4 | 0.53 | 5.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 100
2021-08-30 | 7.5 | 197 | 103 | 824 | 229 | 29 | 13.4 | 2.02 | 6.56 | N/S | 145.15 | 0.5 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 100
2021-08-31 | 7.4 | N/S | N/S | 788 | 190 | 27 | 17.8 | 0.94 | 5.5 | 3.1 | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.049 | <0.002 | 0.004 | 0.058 | 0.88 | 0.18 | <0.002 | 0.076 | N/S | 0.007 | <0.004 | <0.004 | 0.095 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-09-01 | 7.4 | N/S | N/S | 752 | 133 | 25 | 16.1 | 2.64 | 5.21 | N/S | N/S | N/S | N/S | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-02 | 7.4 | N/S | N/S | 856 | 229 | 32 | 18.6 | 1.31 | 6.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-03 | 7.3 | N/S | N/S | 846 | 162 | 25 | 19.3 | 1.99 | 6.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-04 | 7.4 | N/S | N/S | 790 | 140 | 22 | 18.4 | 2.88 | 5.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-05 | 7.3 | 137 | 69 | 782 | 144 | 25 | 19.1 | 1.21 | 5.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 80
2021-09-06 | 7.2 | 209 | 110 | 952 | 283 | 31 | 17.7 | 2.17 | 6.47 | N/S | 138.8 | 0.5 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 104
2021-09-07 | 7.1 | N/S | N/S | 678 | 246 | 31 | 17.4 | 2.06 | 6.6 | 3.63 | N/S | N/S | N/S | N/S | 0.01 | <0.001 | <0.002 | 0.051 | <0.002 | <0.004 | 0.073 | 1.1 | 0.19 | 0.003 | 0.084 | N/S | 0.005 | <0.004 | <0.004 | 0.194 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-09-08 | 7.3 | N/S | N/S | 776 | 146 | T/X | 18.2 | 2.1 | T/X | N/S | N/S | N/S | N/S | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-09 | 7.4 | N/S | N/S | 832 | 192 | T/X | 18.5 | 2.3 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-10 | 7.4 | N/S | N/S | 802 | 188 | 26 | 19.1 | 2.93 | 5.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-11 | 7.3 | N/S | N/S | 750 | 144 | 25 | 19 | 3.04 | 5.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-12 | 7.2 | 153 | 78 | 738 | 176 | 27 | 18 | 1.59 | 6.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2021-09-13 | 7 | 194 | 102 | 790 | 220 | 34 | 21 | <0.25 | 6.66 | N/S | 132.77 | 0.7 | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 100
2021-09-14 | 7.2 | N/S | N/S | 766 | 184 | 30 | 17.9 | 2.37 | 6.42 | 3.95 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.055 | 0.66 | 0.17 | <0.002 | 0.064 | N/S | 0.007 | <0.004 | <0.004 | 0.089 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-09-15 | 7.3 | N/S | N/S | 810 | 192 | 31 | 18.1 | 3.16 | 7.19 | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-16 | 7.3 | N/S | N/S | 778 | 167 | 32 | 19.1 | 2.69 | 7.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-17 | 7.4 | N/S | N/S | 750 | 184 | 27 | 18.7 | 3.63 | 6.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-18 | 7.3 | N/S | N/S | 736 | 166 | 27 | 19 | 2.4 | 5.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-19 | 7.2 | 147 | 75 | 746 | 186 | 29 | 18.4 | 2.04 | 6.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2021-09-20 | 7.3 | 220 | 117 | 812 | 246 | 30 | 18 | 2.16 | 7.16 | N/S | 128.28 | 0.7 | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-09-21 | 7.5 | N/S | N/S | 782 | 208 | 30 | 16.4 | 3.2 | 5.96 | 3.41 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.068 | 0.93 | 0.14 | <0.002 | 0.059 | N/S | 0.008 | <0.004 | <0.004 | 0.109 | 0.002 | <0.002 | <0.002 | <3 | N/S
2021-09-22 | 7.4 | N/S | N/S | 760 | 148 | 27 | 16.4 | 5.08 | 6.52 | N/S | N/S | N/S | N/S | 11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-23 | 7.4 | N/S | N/S | 862 | 238 | 35 | 20.8 | 2.67 | 7.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-24 | 7.3 | N/S | N/S | 744 | 178 | 31 | 18.8 | 3.85 | 6.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-25 | 7.4 | N/S | N/S | 726 | 170 | 28 | 18.5 | 4.03 | 5.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-26 | 7.2 | 152 | 77 | 736 | 168 | 30 | 18.3 | 3.36 | 6.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 85
2021-09-27 | 7.4 | 223 | 118 | 844 | 224 | 27 | 15.8 | 3.64 | 6.83 | N/S | 134.84 | 0.6 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-09-28 | 7.4 | N/S | N/S | 804 | 158 | 30 | 18.9 | 3.41 | 6.43 | 4.1 | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.038 | <0.002 | <0.004 | 0.051 | 0.67 | 0.18 | <0.002 | 0.06 | N/S | 0.006 | <0.004 | <0.004 | 0.095 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-09-29 | 7.3 | N/S | N/S | 800 | 200 | 32 | 19.3 | 3.29 | 7.34 | N/S | N/S | N/S | N/S | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-09-30 | 7.3 | N/S | N/S | 802 | 206 | 30 | 17.8 | 4.08 | 7.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-01 | 7.3 | N/S | N/S | 770 | 202 | 27 | 17.1 | 4.47 | 6.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-02 | 7.3 | N/S | N/S | 738 | 194 | 27 | 17.6 | 3.74 | 6.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-03 | 7.4 | 290 | 159 | 850 | 316 | 30 | 14.9 | <0.25 | 6.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 129
2021-10-04 | 7.4 | 212 | 112 | 780 | 172 | 35 | 23.3 | <0.25 | 5.06 | N/S | 130.86 | 0.6 | 42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 106
2021-10-05 | 7.3 | N/S | N/S | 760 | 112 | 32 | 22.8 | 1.59 | 5.54 | 3.53 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.055 | 0.59 | 0.24 | <0.002 | 0.06 | N/S | 0.007 | <0.004 | <0.004 | 0.078 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-10-06 | 7.6 | N/S | N/S | 822 | 198 | 38 | 25.2 | 1.41 | 6.43 | N/S | N/S | N/S | N/S | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-07 | 7.3 | N/S | N/S | 820 | 260 | 32 | 18.3 | 3.73 | 6.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-08 | 7.4 | N/S | N/S | 842 | 262 | 26 | 18.5 | 2.89 | 4.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-09 | 7.3 | N/S | N/S | 778 | 180 | 33 | 21.3 | 1.62 | 6.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-10 | 7.3 | 202 | 107 | 738 | 140 | 33 | 23 | 0.25 | 4.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2021-10-11 | 7.2 | 228 | 122 | 764 | 196 | 34 | 21.9 | 0.49 | 6.23 | N/S | 123.99 | 0.6 | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 110
2021-10-12 | 7.5 | N/S | N/S | 830 | 217 | 26 | 13.7 | 1.08 | 4.78 | 2.2 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.056 | <0.002 | 0.004 | 0.082 | 1.25 | 0.09 | 0.003 | 0.065 | N/S | 0.006 | <0.004 | <0.004 | 0.135 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-10-13 | 7.5 | N/S | N/S | 768 | 171 | 26 | 15.3 | 1.85 | 5.5 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-14 | 7.4 | N/S | N/S | 744 | 137 | 24 | 14.9 | 0.95 | 4.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-15 | 7.4 | N/S | N/S | 756 | 98 | 26 | 17.5 | 0.92 | 5.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-16 | 7.4 | N/S | N/S | 758 | 100 | 29 | 18.9 | 1.41 | 6.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-17 | 7.3 | 154 | 79 | 720 | 82 | 30 | 22.6 | 0.66 | 5.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2021-10-18 | 7.3 | 157 | 80 | 710 | 100 | 32 | 23.9 | <0.25 | 5.65 | N/S | 146.08 | 0.6 | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2021-10-19 | 7.3 | N/S | N/S | 770 | 142 | 32 | 22.1 | 0.8 | 6.44 | 4.66 | N/S | N/S | N/S | N/S | <0.005 | 0.001 | <0.002 | 0.048 | <0.002 | <0.004 | 0.062 | 0.9 | 0.2 | <0.002 | 0.074 | N/S | 0.007 | <0.004 | <0.004 | 0.071 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-10-20 | 7.2 | N/S | N/S | 780 | 152 | 33 | 22.8 | 1.19 | 6.53 | N/S | N/S | N/S | N/S | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-21 | 7.3 | N/S | N/S | 794 | 148 | 34 | 24.8 | 0.74 | 7.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-22 | 7.2 | N/S | N/S | 750 | 144 | 34 | 24.5 | 1.69 | 6.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-23 | 7.2 | N/S | N/S | 734 | 118 | 34 | 26.1 | 0.86 | 6.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-24 | 7 | 564 | 332 | 946 | 372 | 48 | 26.9 | <0.25 | 9.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 197
2021-10-25 | 7.5 | 238 | 128 | 704 | 232 | 16 | 7.3 | 2 | 3.14 | N/S | 102.02 | 0.3 | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 114
2021-10-26 | 7.7 | N/S | N/S | 720 | 88 | 16 | 10.8 | 0.86 | 2.64 | 1.43 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.047 | <0.002 | <0.004 | 0.036 | 0.68 | 0.13 | <0.002 | 0.047 | N/S | 0.004 | <0.004 | <0.004 | 0.049 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-10-27 | 7.6 | N/S | N/S | 788 | 108 | 22 | 14.5 | 0.95 | 3.61 | N/S | N/S | N/S | N/S | 10 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-28 | 7.5 | N/S | N/S | 788 | 148 | 24 | 16.3 | 1.01 | 4.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-29 | 7.6 | N/S | N/S | 768 | 228 | 16 | 10.9 | 1.54 | 2.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-30 | 7.7 | N/S | N/S | 690 | 93 | 12 | 9.2 | 1.46 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-10-31 | 7.6 | 99 | 48 | 708 | 79 | 20 | 13.5 | 0.66 | 3.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 65
2021-11-01 | 7.5 | 52 | 24 | 762 | 118 | 21 | 13.7 | 2.25 | 4.15 | N/S | 154.25 | 0.5 | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 43
2021-11-02 | 7.5 | N/S | N/S | 770 | 110 | 23 | 15.5 | 2.03 | 4.52 | 2.72 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.043 | <0.002 | <0.004 | 0.042 | 0.62 | 0.14 | <0.002 | 0.06 | N/S | 0.009 | <0.004 | <0.004 | 0.054 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-11-03 | 7.5 | N/S | N/S | 722 | 62 | 23 | 15.9 | 2.34 | 4.51 | N/S | N/S | N/S | N/S | 27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-04 | 7.4 | N/S | N/S | 754 | 100 | 29 | 21.6 | <0.25 | 4.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-05 | 7.4 | N/S | N/S | 780 | 120 | 24 | 19 | 0.63 | 5.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-06 | 7.5 | N/S | N/S | 742 | 81 | 26 | 19.4 | 2.57 | 5.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-07 | 7.4 | 203 | 107 | 808 | 142 | 30 | 19.3 | 3.54 | 6.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 103
2021-11-08 | 7.3 | 290 | 159 | 824 | 194 | 38 | 23.2 | <0.25 | 6.6 | N/S | 147.08 | 0.6 | 51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 129
2021-11-09 | 7.3 | N/S | N/S | 824 | 144 | 34 | 22.1 | 1.41 | 6.23 | 4.06 | N/S | N/S | N/S | N/S | 0.006 | <0.001 | <0.002 | 0.048 | <0.002 | <0.004 | 0.061 | 0.92 | 0.23 | 0.002 | 0.071 | N/S | 0.008 | <0.004 | <0.004 | 0.088 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-11-10 | 7.3 | N/S | N/S | 754 | 132 | 32 | 21.6 | 2.4 | 6.32 | N/S | N/S | N/S | N/S | 42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-11 | 7.5 | N/S | N/S | 800 | 184 | 35 | 21.6 | 0.92 | 6.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-12 | 7.4 | N/S | N/S | 906 | 270 | 22 | 15.9 | 1.57 | 4.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-13 | 7.3 | N/S | N/S | 794 | 162 | 25 | 18.3 | 2.64 | 5.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-14 | 7.4 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X
2021-11-15 | 7.4 | 180 | 94 | 820 | 142 | 31 | 18.8 | 2.06 | 5.88 | N/S | 147.03 | 0.6 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 95
2021-11-16 | 7.4 | N/S | N/S | 776 | 122 | 30 | 21.2 | 1.72 | 5.74 | 3.67 | N/S | N/S | N/S | N/S | 0.005 | <0.001 | <0.002 | 0.044 | <0.002 | <0.004 | 0.051 | 0.7 | 0.2 | <0.002 | 0.071 | N/S | 0.007 | <0.004 | <0.004 | 0.076 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-11-17 | 7.3 | N/S | N/S | 764 | 118 | 29 | 18.9 | 2.99 | 6.68 | N/S | N/S | N/S | N/S | 13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-18 | 7.4 | N/S | N/S | 780 | 132 | 30 | 19 | 1.82 | 6.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-19 | 7.3 | N/S | N/S | 770 | 114 | 29 | 21.7 | 1.62 | 6.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-20 | 7.2 | N/S | N/S | 780 | 142 | 34 | 21.9 | 1.64 | 6.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-21 | 7.3 | 225 | 120 | 760 | 120 | 35 | 23.2 | 0.93 | 6.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 110
2021-11-22 | 7 | 801 | 490 | 976 | 304 | 42 | 25.4 | 0.42 | 7.51 | N/S | 140.25 | 0.6 | 51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 246
2021-11-23 | 7.3 | N/S | N/S | 776 | 124 | 31 | 22.4 | 1.5 | 5.63 | 3.72 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.042 | <0.002 | 0.005 | 0.065 | 0.79 | 0.19 | <0.002 | 0.067 | N/S | 0.018 | <0.004 | <0.004 | 0.088 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-11-24 | 7.4 | N/S | N/S | 766 | 132 | 35 | 24.4 | 0.26 | 5.67 | N/S | N/S | N/S | N/S | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-25 | 7.2 | N/S | N/S | 706 | 94 | 29 | 18.9 | 2.98 | 5.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-26 | 7.2 | N/S | N/S | 704 | 92 | 34 | 25.8 | 1.15 | 5.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-27 | 7.2 | N/S | N/S | 730 | 114 | 38 | 26.2 | 1.58 | 6.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-11-28 | 7.2 | 277 | 151 | 748 | 164 | 39 | 24.1 | 1.79 | 6.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 125
2021-11-29 | 7.4 | 266 | 145 | 776 | 174 | 32 | 19.8 | 3.72 | 6.03 | N/S | 135.82 | 0.6 | 64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 122
2021-11-30 | 7.3 | N/S | N/S | 764 | 124 | 33 | 23.1 | 1.54 | 5.78 | 3.8 | N/S | N/S | N/S | N/S | <0.005 | 0.001 | <0.002 | 0.041 | <0.002 | 0.01 | 0.06 | 0.63 | 0.21 | <0.002 | 0.066 | N/S | 0.015 | <0.004 | <0.004 | 0.074 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-12-01 | 7.3 | N/S | N/S | 736 | 102 | 31 | 20.9 | 4.22 | 5.84 | N/S | N/S | N/S | N/S | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-02 | 7.2 | N/S | N/S | 768 | 130 | 35 | 22.8 | 2.78 | 6.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-03 | 7.2 | N/S | N/S | 778 | 176 | 36 | 24.8 | 1.56 | 7.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-04 | 7.1 | N/S | N/S | 750 | 150 | 33 | 22.6 | 3.01 | 6.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-05 | 7.1 | 209 | 110 | 706 | 122 | 33 | 22.3 | 2.92 | 6.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 105
2021-12-06 | 7.3 | 202 | 106 | 770 | 142 | 32 | 20.9 | 2.24 | 5.96 | N/S | 142.8 | 0.6 | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2021-12-07 | 7.2 | N/S | N/S | 778 | 133 | 30 | 18.5 | 3.52 | 5.9 | 3.76 | N/S | N/S | N/S | N/S | 0.005 | 0.001 | <0.002 | 0.042 | <0.002 | <0.004 | 0.061 | 0.75 | 0.17 | <0.002 | 0.069 | N/S | 0.008 | <0.004 | <0.004 | 0.095 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-12-08 | 7.3 | N/S | N/S | 722 | 120 | 28 | 16.1 | 5.82 | 5.89 | N/S | N/S | N/S | N/S | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-09 | 7.3 | N/S | N/S | 750 | 114 | 31 | 20.6 | 4.4 | 6.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-10 | 7.1 | N/S | N/S | 924 | 326 | 42 | 24.3 | 2.09 | 8.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-11 | 7.4 | N/S | N/S | 904 | 354 | 22 | 14.2 | 1.28 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-12 | 7.4 | 98 | 48 | 688 | 76 | 21 | 14 | 2.14 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 65
2021-12-13 | 7.5 | 117 | 58 | 750 | 78 | 25 | 17.2 | 1.54 | 3.51 | N/S | 145.69 | 0.6 | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 72
2021-12-14 | 7.5 | N/S | N/S | 738 | 80 | 25 | 16.8 | 2.38 | 3.66 | 2.08 | N/S | N/S | N/S | N/S | <0.005 | 0.001 | <0.002 | 0.04 | <0.002 | <0.004 | 0.041 | 0.51 | 0.17 | <0.002 | 0.053 | N/S | 0.006 | <0.004 | <0.004 | 0.054 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-12-15 | 7.5 | N/S | N/S | 790 | 152 | 22 | 15.8 | 3.19 | 4.02 | N/S | N/S | N/S | N/S | 24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-16 | 7.5 | N/S | N/S | 764 | 112 | 22 | 16.2 | 3.75 | 5.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-17 | 7.5 | N/S | N/S | 736 | 108 | 28 | 23.3 | 0.41 | 5.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-18 | 7.4 | N/S | N/S | 748 | 108 | 28 | 22.3 | 1.71 | 5.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-19 | 7.4 | 178 | 93 | 750 | 126 | 30 | 21.7 | 1.81 | 5.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 94
2021-12-20 | 7.4 | 220 | 117 | 772 | 138 | 35 | 22.2 | 0.98 | 6.24 | N/S | 145.66 | 0.6 | 40 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2021-12-21 | 7.4 | N/S | N/S | 760 | 122 | 33 | 21.2 | 1.89 | 6.49 | 4.41 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.045 | <0.002 | <0.004 | 0.055 | 0.69 | 0.17 | <0.002 | 0.089 | N/S | 0.009 | <0.004 | <0.004 | 0.072 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-12-22 | 7.3 | N/S | N/S | 824 | 174 | 31 | 18.6 | 3.55 | 6.91 | N/S | N/S | N/S | N/S | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-23 | 7.4 | N/S | N/S | 746 | 122 | 31 | 23.8 | 0.84 | 6.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-24 | 7.2 | N/S | N/S | 758 | 134 | 32 | 24.5 | 0.9 | 5.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-25 | 7.2 | N/S | N/S | 748 | 134 | 31 | 23.2 | 2.6 | 5.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-26 | 7.2 | 343 | 192 | 822 | 238 | 38 | 25.1 | 1.66 | 6.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 143
2021-12-27 | 7.2 | 303 | 167 | 866 | 328 | 28 | 14.8 | 1.09 | 5.01 | N/S | 118.04 | 0.4 | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 132
2021-12-28 | 7.7 | N/S | N/S | 778 | 174 | 23 | 14.3 | 1 | 3.82 | 2.08 | N/S | N/S | N/S | N/S | <0.005 | <0.001 | <0.002 | 0.045 | <0.002 | <0.004 | 0.056 | 0.75 | 0.14 | <0.002 | 0.066 | N/S | 0.005 | <0.004 | <0.004 | 0.084 | <0.002 | <0.002 | <0.002 | <3 | N/S
2021-12-29 | 7.5 | N/S | N/S | 878 | 166 | 23 | 14 | 0.45 | 3.81 | N/S | N/S | N/S | N/S | 17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-30 | 7.6 | N/S | N/S | 828 | 120 | 19 | 13 | 1.48 | 3.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2021-12-31 | 7.7 | N/S | N/S | 884 | 138 | 19 | 14.6 | 0.85 | 3.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
Reporting Limit |  | 2 | 2 | 25 | 2 | 1 | 0.3 | 0.25 | 0.15 | 0.15 | 0.5 | 0.1 | 5 | 5 | 0.005 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.5 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 5
Observations | 365 | 107 | 41 | 358 | 358 | 225 | 332 | 333 | 225 | 30 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 39 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 109
Minimum | 6.6 | 52 | 24 | 672 | 62 | 12 | 6 | <0.25 | 1.91 | 1.12 | 102.02 | 0.3 | 9 | 6 | <0.005 | <0.001 | <0.002 | 0.037 | <0.002 | <0.004 | 0.027 | 0.4 | 0.08 | <0.002 | 0.047 | <0.5 | 0.004 | <0.004 | <0.004 | 0.043 | <0.002 | <0.002 | <0.002 | <3 | 43
Mean | 7.4 | 192 | 128 | 893 | 177 | 30 | 17.8 | <2.07 | 6.02 | 3.66 | 191.06 | 0.6 | 36 | 27 | <0.006 | <0.001 | <0.001 | 0.051 | <0.001 | <0.004 | 0.064 | 0.89 | 0.17 | <0.002 | 0.072 | <0.4 | 0.009 | <0.003 | <0.003 | 0.102 | <0.001 | <0.001 | <0.001 | <2 | 99
Maximum | 7.7 | 801 | 490 | 1894 | 721 | 56 | 27.4 | 5.82 | 11.2 | 5.17 | 476.71 | 0.7 | 70 | 46 | 0.017 | <0.005 | <0.002 | 0.135 | <0.002 | 0.015 | 0.288 | 4.17 | 0.31 | 0.01 | 0.113 | <0.5 | 0.022 | 0.004 | <0.004 | 0.436 | <0.002 | <0.002 | <0.002 | <3 | 245
*Effective 1/1/21, means are no longer calculated using the Reporting Limit value in place of non-detect/<LOQ results and are now calculated by replacing any non-detect/<LOQ results with the Reporting Limit/(SQRT2).
**Effective 8/1/21, BOD5 and CBOD5 calculated from TOC result.
January-February 2021, NH3, NO2+NO3, T/X: Minimal staffing due to COVID-19.
January-March 2021, Tot Hg, T/X: Calibration expired for thermocouple used to track digestion.
January 11, 2021, Tot Hg, T/X: Sample never arrived at laboratory. Resampled next day.
February 16, 2021, Cr6+, S/X: Holding time exceeded, resampled.
March 21, 22, 2021, BOD5, T/X: Temperature of incubator outside of acceptable range.
May 2, 2021, All analyses, S/X: Sample did not meet thermal preservation requirements when delivered to lab.
May 17, 23, 2021, BOD5, T/X: Temperature of incubator outside of acceptable range.
May 25, 2021, NH3, T/X: Precision failure. Retest did not confirm results.
June 3, 2021, TKN, TOT PHOS, T/X: Thermal preservation lost due to cooler malfunction.
June 4, 2021, TS, SS, T/X: Thermal preservation lost due to cooler malfunction.
June 5, 2021, TS, SS, NH3, NO2+NO3, T/X: Thermal preservation lost due to cooler malfunction.
June 8, 2021, CN, CN-WAD: Sample MS recovery failed, but LCS passed.
June 19, 26, 2021, All analyses, S/X: Thermal preservation lost due to cooler malfunction.
July 29, 2021, TKN, P-TOT, T/X: Thermal presevation lost due to cooler malfunction.
July 30, 2021, TS, SS, T/X: Thermal presevation lost due to cooler malfunction.
August 7, 8, 10, 11, 12, 2021, TKN, P-TOT, T/X: Thermal presevation lost due to cooler malfunction.
August 10, 2021, P-SOL, T/X: Thermal presevation lost due to cooler malfunction.
August 11-13, 2021, BOD5, CBOD5, TOC, T/X: Thermal presevation lost due to cooler malfunction.
August 13, 2021, NH3, NO2+NO3, T/X: Thermal presevation lost due to cooler malfunction.
August 17-21, 24-28, 2021, BOD5, CBOD5, TOC, T/X: Test not needed.
August 28, 2021, TKN, P-TOT, NH3, NO2+NO3, T/X: Thermal presevation lost due to cooler malfunction.
September 8-9, 2021, TKN, P-TOT, T/X: Thermal presevation lost due to cooler malfunction.
September 27, 2021, FOG, T/X: LCS Failure
November 14, 2021, S/X: Sample was not representative and cancelled by M&O.

## Egan Raw 2022
| pH | BOD5 | CBOD5 | TS | SS | TKN | NH3-N | NO2+NO3 | P-TOT | P-SOL | Cl | F | FOG | Phenol-Man | CN-AMEN | CN (GRAB) | As | Ba | Cd | Cr_Tot | Cu | Fe_Tot | Fe_Sol | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr_+6 | TOC
Date |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | MG/L | mg/L | mg/L | mg/L | ug/L | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L
2022-01-01 | 7.5 | N/S | N/S | 842 | 150 | 17 | 12.8 | 2.1 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-02 | 7.8 | 111 | 55 | 872 | 144 | 24 | 15.2 | 1.19 | 4.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2022-01-03 | 7.5 | 84 | 40 | 854 | 86 | 20 | 14.3 | 2.17 | 3.81 | N/S | 225.96 | 0.5 | 26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 59
2022-01-04 | 7.4 | N/S | N/S | 856 | 132 | 27 | 17.6 | 0.34 | 4.64 | 2.73 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.045 | <0.002 | <0.004 | 0.048 | 0.69 | 0.15 | <0.002 | 0.07 | N/S | 0.007 | <0.004 | <0.004 | 0.076 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-01-05 | 7.5 | N/S | N/S | 828 | 94 | 23 | 15.2 | 2.7 | 4.61 | N/S | N/S | N/S | N/S | 8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-06 | 7.5 | N/S | N/S | 804 | 86 | 21 | 15.1 | 3.79 | 4.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-07 | 7.6 | N/S | N/S | 766 | 96 | 23 | 18.8 | 1.82 | 3.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-08 | 7.5 | N/S | N/S | 758 | 130 | 23 | 18.5 | 2.64 | 4.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-09 | 7.5 | 203 | 107 | 826 | 142 | 28 | 19.1 | 1.86 | 5.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 103
2022-01-10 | 7.4 | 178 | 92 | 772 | 106 | 29 | 22 | 1.22 | 5.01 | N/S | 168.51 | 0.6 | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 94
2022-01-11 | 7.4 | N/S | N/S | 806 | 126 | 26 | 19.2 | 1.86 | 5.08 | 3.41 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.042 | <0.002 | <0.004 | 0.057 | 0.67 | 0.2 | <0.002 | 0.077 | N/S | 0.006 | <0.004 | <0.004 | 0.088 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-01-12 | 7.3 | N/S | N/S | 840 | 146 | 29 | 17.4 | 3.55 | 6.23 | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-13 | 7.3 | N/S | N/S | 868 | 130 | 30 | 21.7 | 1.29 | 6.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-14 | 7.4 | N/S | N/S | 836 | 152 | 24 | 18.5 | 3.77 | 4.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-15 | 7.4 | N/S | N/S | 816 | 156 | 30 | 21.4 | 2.36 | 5.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-16 | 7.4 | 223 | 118 | 806 | 170 | 30 | 23.4 | 0.58 | 5.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 109
2022-01-17 | 7.5 | 192 | 100 | 886 | 224 | 34 | 22 | 1.07 | 6.13 | N/S | 181.59 | 0.7 | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 99
2022-01-18 | 7.5 | N/S | N/S | 806 | 134 | 32 | 19 | 2.63 | 6.02 | 3.99 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.045 | <0.002 | <0.004 | 0.056 | 0.72 | 0.19 | <0.002 | 0.069 | N/S | 0.006 | <0.004 | <0.004 | 0.09 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-01-19 | 7.4 | N/S | N/S | 826 | 136 | 32 | 19.3 | 2.53 | 5.96 | N/S | N/S | N/S | N/S | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-20 | 7.4 | N/S | N/S | 800 | 124 | 28 | 18.3 | 3.15 | 6.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-21 | 7.5 | N/S | N/S | 754 | 144 | 23 | 17.1 | 5.4 | 5.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-22 | 7.2 | N/S | N/S | 794 | 166 | 34 | 21.7 | 2.65 | 6.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-23 | 7.3 | 388 | 219 | 840 | 216 | 42 | 25.5 | 0.55 | 6.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 155
2022-01-24 | 7.3 | 179 | 93 | 806 | 160 | 30 | 17.6 | 3.67 | 6.51 | N/S | 167.04 | 0.7 | 47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 95
2022-01-25 | 7 | N/S | N/S | 754 | 246 | 38 | 22.9 | 1 | 6.93 | 3.92 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.064 | <0.002 | 0.008 | 0.102 | 1.15 | 0.26 | 0.003 | 0.086 | N/S | 0.011 | <0.004 | <0.004 | 0.14 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-01-26 | 7.4 | N/S | N/S | 838 | 164 | 37 | 24.7 | 0.51 | 6.2 | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-27 | 7.4 | N/S | N/S | 824 | 156 | 34 | 21.4 | 1.85 | 6.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-28 | 7.3 | N/S | N/S | 786 | 134 | 30 | 19.1 | 3.86 | 5.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-29 | 7.3 | N/S | N/S | 838 | 166 | 34 | 26.4 | 0.92 | 5.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-01-30 | 7.3 | 231 | 123 | 820 | 152 | 36 | 24.3 | 0.49 | 5.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 111
2022-01-31 | 7.1 | 911 | 565 | 1078 | 371 | 42 | 23.7 | 0.92 | 8.39 | N/S | 163.3 | 0.9 | 41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 267
2022-02-01 | 7.5 | N/S | N/S | 896 | 283 | 35 | 21.8 | 1.66 | 7.49 | 4.7 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.049 | <0.002 | 0.005 | 0.083 | 1.08 | 0.22 | <0.002 | 0.074 | N/S | 0.014 | <0.004 | <0.004 | 0.132 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-02-02 | 7.5 | N/S | N/S | 896 | 192 | 33 | 22.1 | 1.79 | 6.64 | N/S | N/S | N/S | N/S | 26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-03 | 7.4 | N/S | N/S | 956 | 174 | 35 | 25.9 | 0.28 | 7.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-04 | 7.4 | N/S | N/S | 858 | 156 | 32 | 23.6 | 1.92 | 6.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-05 | 7.5 | N/S | N/S | 856 | 168 | 30 | 21 | 3.55 | 5.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-06 | 7.4 | 200 | 105 | 834 | 174 | 32 | 21.4 | 2.33 | 5.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2022-02-07 | 7.4 | 271 | 147 | 888 | 176 | 36 | 23.3 | 1.11 | 6.16 | N/S | 190.78 | 0.7 | 42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 123
2022-02-08 | 7.5 | N/S | N/S | 868 | 166 | 29 | 17.8 | 4.45 | 6.56 | 4.12 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.051 | <0.002 | 0.008 | 0.074 | 0.87 | 0.2 | <0.002 | 0.063 | N/S | 0.008 | <0.004 | <0.004 | 0.105 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-02-09 | 7.3 | N/S | N/S | 1010 | 233 | 39 | 25.4 | 0.43 | 7.33 | N/S | N/S | N/S | N/S | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-10 | 6.8 | N/S | N/S | 1424 | 583 | 46 | 23.6 | 1.06 | 8.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-11 | 7.4 | N/S | N/S | 1070 | 96 | 27 | 21.3 | 1.14 | 5.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-12 | 7.5 | N/S | N/S | 1193 | 160 | 26 | 19.6 | 0.88 | 4.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-13 | 7.5 | 166 | 86 | 988 | 94 | 27 | 18.4 | 2.38 | 4.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 90
2022-02-14 | 7.5 | 155 | 80 | 1028 | 122 | 27 | 17.6 | 3.68 | 4.88 | N/S | 255.18 | 0.6 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2022-02-15 | 7.1 | N/S | N/S | 1203 | 404 | 36 | 17.5 | 3.82 | 7.14 | 3.66 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.072 | <0.002 | 0.01 | 0.133 | 2.24 | 0.2 | 0.003 | 0.083 | N/S | 0.012 | <0.004 | <0.004 | 0.2 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-02-16 | 7.6 | N/S | N/S | 920 | 174 | 32 | 19.6 | 1 | 5.34 | N/S | N/S | N/S | N/S | 26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-17 | 7.7 | N/S | N/S | 1176 | 182 | 18 | 8.9 | 1.81 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-18 | 7.8 | N/S | N/S | 1114 | 122 | 18 | 12.2 | 1.93 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-19 | 7.5 | N/S | N/S | 1090 | 104 | 20 | 13.4 | 1.91 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-20 | 7.5 | 148 | 75 | 1078 | 142 | 27 | 15.7 | 0.97 | 4.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2022-02-21 | 7.5 | 94 | 46 | 1040 | 92 | 22 | 14.5 | 1.65 | 3.71 | N/S | 352.85 | 0.6 | 27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 63
2022-02-22 | 7.6 | N/S | N/S | 1199 | 224 | 22 | 11.8 | 0.66 | 4.34 | 1.76 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.071 | <0.002 | 0.007 | 0.071 | 1.58 | 0.18 | 0.005 | 0.065 | N/S | 0.006 | <0.004 | <0.004 | 0.102 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-02-23 | 7.7 | N/S | N/S | 1161 | 120 | 16 | 9.8 | 2.1 | 2.98 | N/S | N/S | N/S | N/S | 5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-24 | 7.5 | N/S | N/S | 1078 | 90 | 18 | 12.9 | 1.74 | 3.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-25 | 7.6 | N/S | N/S | 1060 | 63 | 19 | 14.2 | 1.99 | 3.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-26 | 7.6 | N/S | N/S | 1101 | 130 | 21 | 14.5 | 2.72 | 4.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-02-27 | 7.5 | 156 | 80 | 1086 | 128 | 27 | 17.1 | 0.69 | 4.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2022-02-28 | 7.4 | 154 | 79 | 1046 | 122 | 27 | 15.2 | 0.3 | 4.61 | N/S | 307.38 | 0.6 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2022-03-01 | 7.5 | N/S | N/S | 1161 | 128 | 25 | 15.8 | 1.77 | 4.89 | 2.99 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.057 | <0.002 | 0.004 | 0.053 | 0.81 | 0.17 | <0.002 | 0.07 | N/S | 0.005 | <0.004 | <0.004 | 0.075 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-03-02 | 7.5 | N/S | N/S | 1236 | 122 | 24 | 14.6 | 1.92 | 4.84 | N/S | N/S | N/S | N/S | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-03 | 7.5 | N/S | N/S | 1224 | 154 | 23 | 15.7 | 1.87 | 5.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-04 | 7.5 | N/S | N/S | 1132 | 120 | 22 | 15.3 | 1.7 | 4.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-05 | 7.6 | N/S | N/S | 1152 | 190 | 28 | 15 | 2.17 | 5.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-06 | 7.6 | 167 | 86 | 1134 | 152 | 25 | 15.2 | 0.71 | 4.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 91
2022-03-07 | 7.6 | 250 | 135 | 1392 | 244 | 26 | 13.5 | 1.18 | 5.29 | N/S | 421.85 | 0.5 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 117
2022-03-08 | 7.8 | N/S | N/S | 1320 | 208 | 23 | 13.8 | 0.97 | 5.14 | 2.78 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.072 | <0.002 | 0.005 | 0.067 | 1.06 | 0.15 | <0.002 | 0.074 | N/S | 0.014 | <0.004 | <0.004 | 0.103 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-03-09 | 7.2 | N/S | N/S | 1432 | 308 | 27 | 12 | 2.62 | 5.73 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-10 | 7.6 | N/S | N/S | 1074 | 70 | 19 | 13.6 | 2.41 | 4.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-11 | 7.6 | N/S | N/S | 1038 | 100 | 21 | 16 | 2.32 | 3.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-12 | 7.6 | N/S | N/S | 1008 | 98 | 26 | 16.7 | 1.71 | 4.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-13 | 7.5 | 172 | 89 | 970 | 106 | 27 | 18.1 | 0.4 | 4.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 92
2022-03-14 | 7.6 | 193 | 101 | 880 | 144 | 27 | 17.7 | 1.3 | 4.96 | N/S | 265.05 | 0.6 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 99
2022-03-15 | 7.5 | N/S | N/S | 982 | 102 | 27 | 18.9 | 1.07 | 4.79 | 3.27 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.045 | <0.002 | <0.004 | 0.054 | 0.6 | 0.19 | <0.002 | 0.078 | N/S | 0.005 | <0.004 | <0.004 | 0.064 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-03-16 | 7.5 | N/S | N/S | 998 | 154 | 29 | 17.1 | 3.06 | 5.75 | N/S | N/S | N/S | N/S | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-17 | 7.6 | N/S | N/S | 1023 | 164 | 34 | 21.9 | 2.63 | 7.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-18 | 7.5 | N/S | N/S | 1098 | 212 | 42 | 27.9 | 1.39 | 8.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-19 | 7.5 | N/S | N/S | 1152 | 178 | 19 | 13.3 | 3.44 | 3.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-20 | 7.7 | 127 | 63 | 1190 | 128 | 24 | 14.2 | 0.79 | 4.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2022-03-21 | 7.6 | 105 | 52 | 1106 | 100 | 22 | 13.4 | 1.98 | 3.98 | N/S | 292.62 | 0.5 | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2022-03-22 | 7.5 | N/S | N/S | 1146 | 176 | 27 | 15.2 | 1.12 | 4.96 | 2.81 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.06 | <0.002 | <0.004 | 0.054 | 0.84 | 0.16 | <0.002 | 0.079 | N/S | 0.006 | <0.004 | <0.004 | 0.083 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-03-23 | 7.5 | N/S | N/S | 1260 | 260 | 25 | 12.1 | 1.18 | 4.93 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-24 | 7.6 | N/S | N/S | 1089 | 138 | 16 | 10 | 2.43 | 3.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-25 | 7.6 | N/S | N/S | 984 | 92 | 16 | 10.7 | 1.59 | 2.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-26 | 7.7 | N/S | N/S | 1033 | 120 | 17 | 12.1 | 1.54 | 2.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-27 | 7.5 | 103 | 51 | 1000 | 124 | 23 | 13.5 | 2.03 | 3.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 67
2022-03-28 | 7.4 | 120 | 60 | 1026 | 136 | 24 | 15.9 | 0.85 | 3.74 | N/S | 246.93 | 0.6 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 73
2022-03-29 | 7.5 | N/S | N/S | 992 | 122 | 24 | 14.9 | 2.69 | 4.64 | 2.91 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.055 | <0.002 | <0.004 | 0.047 | 0.75 | 0.12 | <0.002 | 0.079 | N/S | 0.007 | <0.004 | <0.004 | 0.073 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-03-30 | 7.4 | N/S | N/S | 1065 | 240 | 30 | 17.5 | <0.25 | 5.73 | N/S | N/S | N/S | N/S | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-03-31 | 7.5 | N/S | N/S | 964 | 152 | 19 | 10.1 | 1.48 | 3.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-01 | 7.6 | N/S | N/S | 1016 | 126 | 15 | 10.3 | 1.88 | 2.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-02 | 7.4 | N/S | N/S | 990 | 130 | 16 | 11.7 | 1.27 | 2.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-03 | 7.5 | 78 | 37 | 964 | 114 | 17 | 10.1 | 1.45 | 2.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 56
2022-04-04 | 7.6 | 96 | 47 | 948 | 120 | 17 | 9.9 | 1.21 | 3.1 | N/S | 220.09 | 0.4 | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 64
2022-04-05 | 7.6 | N/S | N/S | 946 | 76 | 17 | 11 | 1.38 | 2.92 | 1.66 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.048 | <0.002 | <0.004 | 0.033 | 0.55 | 0.11 | <0.002 | 0.063 | N/S | 0.003 | <0.004 | <0.004 | 0.045 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-04-06 | 7.6 | N/S | N/S | 858 | 102 | 15 | 9.2 | 1.42 | 2.39 | N/S | N/S | N/S | N/S | 7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-07 | 7.7 | N/S | N/S | 926 | 92 | 15 | 9.1 | 1.73 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-08 | 7.7 | N/S | N/S | 928 | 97 | 17 | 10.6 | 1.69 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-09 | 7.6 | N/S | N/S | 928 | 108 | 16 | 10.9 | 1.91 | 2.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-10 | 7.6 | 126 | 63 | 986 | 138 | 25 | 13.3 | 0.34 | 4.11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2022-04-11 | 7.6 | 90 | 44 | 1016 | 126 | 23 | 13.2 | 1.63 | 4.23 | N/S | 234.37 | 0.5 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2022-04-12 | 7.5 | N/S | N/S | 950 | 132 | 23 | 17.2 | 0.42 | 4.21 | 3.09 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.052 | <0.002 | <0.004 | 0.046 | 0.65 | 0.15 | <0.002 | 0.077 | N/S | 0.007 | <0.004 | <0.004 | 0.06 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-04-13 | 7.6 | N/S | N/S | 1022 | 240 | 29 | 14.4 | 0.84 | 5.81 | N/S | N/S | N/S | N/S | 13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-14 | 7.7 | N/S | N/S | 842 | 108 | 17 | 10.1 | 1.2 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-15 | 7.5 | N/S | N/S | 870 | 98 | 16 | 11.3 | 1.92 | 3.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-16 | 7.6 | N/S | N/S | 900 | 102 | 20 | 14.6 | 0.94 | 3.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-17 | 7.5 | 77 | 37 | 868 | 100 | 20 | 14.2 | 0.41 | 3.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 55
2022-04-18 | 7.5 | 71 | 33 | 936 | 108 | 20 | 14.7 | 1.22 | 3.56 | N/S | 211.41 | 0.5 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 53
2022-04-19 | 7.5 | N/S | N/S | 880 | 92 | 19 | 14 | 0.69 | 3.75 | 2.74 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.039 | <0.002 | <0.004 | 0.026 | 0.4 | 0.09 | <0.002 | 0.067 | N/S | 0.008 | <0.004 | <0.004 | 0.628 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-04-20 | 7.4 | N/S | N/S | 946 | 148 | 24 | 16 | 0.42 | 4.75 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-21 | 7.5 | N/S | N/S | 910 | 152 | 23 | 13.2 | 0.39 | 4.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-22 | 7.3 | N/S | N/S | 842 | 210 | 16 | 11.9 | 1.84 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-23 | 7.6 | N/S | N/S | 754 | 90 | 12 | 7 | 2.77 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-24 | 7.5 | 105 | 52 | 852 | 142 | 19 | 11.4 | 1.12 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2022-04-25 | 7.7 | 78 | 37 | 948 | 156 | 25 | 13.9 | 1.53 | 4.56 | N/S | 194.93 | 0.5 | 19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 56
2022-04-26 | 7.7 | N/S | N/S | 892 | 84 | 20 | 13.4 | 1.7 | 3.3 | 1.97 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.047 | <0.002 | <0.004 | 0.03 | 0.61 | T/X | <0.002 | 0.068 | N/S | 0.006 | <0.004 | 0.004 | 0.039 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-04-27 | 7.5 | N/S | N/S | 888 | 108 | 21 | 14.6 | 1.12 | 3.52 | N/S | N/S | N/S | N/S | 7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-28 | 7.5 | N/S | N/S | 896 | 100 | 22 | 14.6 | 2.05 | 3.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-29 | 7.5 | N/S | N/S | 918 | 117 | 21 | 15.5 | 2.37 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-04-30 | 7.5 | N/S | N/S | 1678 | 875 | 42 | 18.3 | <0.25 | 8.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-01 | 7.7 | 80 | 38 | 796 | 110 | 19 | 11.7 | 0.99 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 57
2022-05-02 | 7.6 | 105 | 51 | 866 | 150 | 21 | 13.3 | 1.42 | 3.59 | N/S | 183.62 | 0.5 | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 67
2022-05-03 | 7.6 | N/S | N/S | 760 | 124 | 15 | 8.7 | 2.03 | 3 | 1.41 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.047 | <0.002 | <0.004 | 0.042 | 1.06 | 0.11 | <0.002 | 0.059 | N/S | 0.005 | <0.004 | <0.004 | 0.064 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-05-04 | 7.6 | N/S | N/S | 836 | 116 | 16 | 9.3 | 1.66 | 3.26 | N/S | N/S | N/S | N/S | <5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-05 | 7.6 | N/S | N/S | 900 | 164 | 21 | 12.4 | 2.35 | 4.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-06 | 7.5 | N/S | N/S | 934 | 116 | 16 | 9.8 | 2.14 | 3.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-07 | 7.6 | N/S | N/S | 968 | 178 | 14 | 9.6 | 1.54 | 2.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-08 | 7.5 | 153 | 78 | 1038 | 188 | 22 | 13.8 | 0.9 | 3.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2022-05-09 | 7.5 | 24 | 10 | 954 | 164 | 23 | 14.1 | 0.64 | 3.73 | N/S | 186.79 | 0.5 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 26
2022-05-10 | 7.5 | N/S | N/S | 936 | 104 | 20 | 13.8 | <0.25 | 3.08 | 1.77 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.043 | <0.002 | <0.004 | 0.041 | 0.33 | 0.08 | <0.002 | 0.061 | N/S | 0.005 | <0.004 | <0.004 | 1.199 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-05-11 | 7.5 | N/S | N/S | 828 | 62 | 20 | 14.5 | <0.25 | 2.91 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-12 | 7.4 | N/S | N/S | 822 | 76 | 22 | 15.2 | <0.25 | 3.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-13 | 7.5 | N/S | N/S | 840 | 112 | 21 | 15.9 | 0.74 | 3.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-14 | 7.4 | N/S | N/S | 906 | 164 | 26 | 17.1 | 0.45 | 4.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-15 | 7.4 | 133 | 67 | 850 | 136 | 25 | 15.3 | 1.1 | 4.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 78
2022-05-16 | 7.5 | 106 | 52 | 868 | 124 | 25 | 16.4 | 1 | 4.21 | N/S | 183.59 | 0.6 | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2022-05-17 | 7.4 | N/S | N/S | 878 | 57 | 26 | 18.4 | 0.93 | 4.98 | 3.32 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.04 | <0.002 | <0.004 | 0.05 | 0.48 | 0.12 | <0.002 | 0.079 | N/S | 0.008 | <0.004 | <0.004 | 0.656 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-05-18 | 7.5 | N/S | N/S | 1022 | 284 | 30 | 17.5 | 2.17 | 5.92 | N/S | N/S | N/S | N/S | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-19 | 7.5 | N/S | N/S | 850 | 140 | 22 | 14.6 | 1.07 | 4.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-20 | 7.4 | N/S | N/S | 1058 | 346 | 22 | 15.9 | 0.87 | 4.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-21 | 7.4 | N/S | N/S | 826 | 220 | 16 | 11.9 | 0.77 | 3.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-22 | 7.5 | 129 | 65 | 844 | 192 | 18 | 11.2 | 1.13 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 77
2022-05-23 | 7.5 | 173 | 90 | 890 | 168 | 21 | 13.1 | 2.23 | 3.77 | N/S | 177.02 | 0.6 | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 93
2022-05-24 | 7.4 | N/S | N/S | 940 | 136 | 22 | 14.4 | 2.27 | 4.19 | 2.57 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.04 | <0.002 | <0.004 | 0.044 | 0.58 | 0.09 | <0.002 | 0.076 | N/S | 0.005 | <0.004 | <0.004 | 0.7 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-05-25 | 7.3 | N/S | N/S | 964 | 228 | 31 | 17.7 | 1.9 | 5.88 | N/S | N/S | N/S | N/S | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-26 | 7.5 | N/S | N/S | 1072 | 316 | 24 | 10.5 | 4.26 | 5.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-27 | 7.5 | N/S | N/S | 1064 | 344 | 26 | 15.6 | 3.22 | 4.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-28 | 7.5 | N/S | N/S | 876 | 178 | 14 | 10.3 | 2.56 | 3.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-05-29 | 7.4 | 58 | 27 | 820 | 105 | 17 | 10.8 | 2.36 | 3.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 46
2022-05-30 | 7.4 | 73 | 34 | 912 | 192 | 19 | 9.7 | 3.11 | 4.38 | N/S | 182.97 | 0.6 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 53
2022-05-31 | 7.5 | N/S | N/S | 844 | 156 | 17 | 9.8 | 3.24 | 4.08 | 2.6 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.044 | <0.002 | <0.004 | 0.041 | 0.65 | 0.12 | <0.002 | 0.071 | N/S | 0.004 | <0.004 | <0.004 | 0.64 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-06-01 | 7.5 | N/S | N/S | 826 | 138 | 17 | 10.2 | 3.39 | 4.31 | N/S | N/S | N/S | N/S | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-02 | 7.4 | N/S | N/S | 928 | 144 | 21 | 11.1 | 4.07 | 5.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-03 | 7.4 | N/S | N/S | 970 | 214 | 17 | 9.7 | 5.28 | 5.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-04 | 7.4 | N/S | N/S | 898 | 152 | 16 | 10.6 | 5.26 | 4.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-05 | 7.4 | 77 | 37 | 860 | 144 | 22 | 12.4 | 3.44 | 5.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 55
2022-06-06 | 7.3 | 186 | 97 | 922 | 216 | 25 | 13.3 | 2.83 | 5.31 | N/S | 171.05 | 0.7 | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 97
2022-06-07 | 7.4 | N/S | N/S | 780 | 92 | 19 | 11.2 | 2.96 | 4.13 | 2.93 | N/S | N/S | N/S | N/S | <0.005 | 0.015 | <0.002 | 0.04 | <0.002 | <0.004 | 0.033 | 0.6 | 0.14 | <0.002 | 0.075 | N/S | 0.004 | <0.004 | <0.004 | 0.624 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-06-08 | 7.3 | N/S | N/S | 932 | 228 | 20 | 10.4 | 2.89 | 4.66 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-09 | 7.2 | N/S | N/S | 912 | 248 | 25 | 11.4 | 2.15 | 6.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-10 | 7.4 | N/S | N/S | 1018 | 168 | 14 | 8.7 | 5.13 | 3.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-11 | 7.5 | N/S | N/S | 908 | 118 | 16 | 10.1 | 4.19 | 3.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-12 | 7.3 | 58 | 27 | 926 | 110 | 19 | 11.2 | 3.8 | 4.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 46
2022-06-13 | 7.4 | 263 | 142 | 1088 | 296 | 22 | 9.5 | 4.61 | 5.28 | N/S | 165.09 | 0.6 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 121
2022-06-14 | 7.6 | N/S | N/S | 1008 | 288 | 19 | 6.4 | 4.23 | 4.34 | 1.99 | N/S | N/S | N/S | N/S | <0.005 | 0.008 | <0.002 | 0.053 | <0.002 | <0.004 | 0.071 | 1.23 | 0.09 | 0.003 | 0.065 | N/S | 0.006 | <0.004 | <0.004 | 1.017 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-06-15 | 7.5 | N/S | N/S | 916 | 230 | 17 | 7.7 | 4.35 | 4.45 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-16 | 7.5 | N/S | N/S | 792 | 142 | 16 | 8.6 | 5.96 | 4.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-17 | 7.4 | N/S | N/S | 810 | 132 | 16 | 9.6 | 5.79 | 4.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-18 | 7.4 | N/S | N/S | 812 | 130 | 25 | 14.1 | 5.13 | 6.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-19 | 7.4 | 93 | 45 | 800 | 126 | 19 | 10.8 | 5.32 | 5.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 62
2022-06-20 | 7.4 | 123 | 61 | 938 | 242 | 22 | 9.9 | 5.25 | 5.84 | N/S | 166.59 | 0.7 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 75
2022-06-21 | 7.4 | N/S | N/S | 878 | 162 | 20 | 10.2 | 4.35 | 5.36 | 3.55 | N/S | N/S | N/S | N/S | <0.005 | 0.007 | <0.002 | 0.042 | <0.002 | <0.004 | 0.048 | 0.62 | 0.13 | <0.002 | 0.07 | N/S | 0.009 | <0.004 | <0.004 | 0.767 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-06-22 | 7.3 | N/S | N/S | 860 | 226 | T/X | 10.2 | 4.01 | T/X | N/S | N/S | N/S | N/S | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-23 | 7.4 | N/S | N/S | 814 | 192 | T/X | 12.3 | 4.18 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-24 | 7.3 | N/S | N/S | T/X | 368 | 33 | 16.4 | 3.72 | 7.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-25 | 7.4 | N/S | N/S | 808 | 160 | 14 | 9.7 | 5.18 | 4.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-26 | 7.4 | 87 | 42 | 738 | 86 | 17 | 10.2 | 4.54 | 4.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 60
2022-06-27 | 7.4 | 97 | 47 | 794 | 116 | 19 | 12 | 4.04 | 5.13 | N/S | 159.47 | 0.7 | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 64
2022-06-28 | 7.3 | N/S | N/S | 780 | 108 | 21 | 12.8 | 3.95 | 5.48 | 4.04 | N/S | N/S | N/S | N/S | <0.005 | 0.009 | <0.002 | 0.033 | <0.002 | <0.004 | 0.033 | 0.51 | 0.17 | <0.002 | 0.074 | N/S | 0.005 | <0.004 | <0.004 | 0.698 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-06-29 | 7.3 | N/S | N/S | 836 | 146 | 24 | 13.3 | 3.83 | 5.95 | N/S | N/S | N/S | N/S | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-06-30 | 7.3 | N/S | N/S | 812 | 176 | T/X | 12 | 4.43 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-01 | 7.2 | N/S | N/S | 1136 | 220 | 14 | 10.3 | 4.88 | 4.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-02 | 7.2 | N/S | N/S | 998 | 128 | 20 | 13 | 4.19 | 5.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-03 | 7.2 | 201 | 106 | 1086 | 246 | 23 | 9.7 | 4.78 | 6.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 102
2022-07-04 | 7.3 | 519 | 303 | 1194 | 440 | 31 | 11.2 | 3.75 | 7.33 | N/S | 147.18 | 0.6 | 40 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 187
2022-07-05 | 7.4 | N/S | N/S | 1908 | 933 | 45 | 8.8 | 1.24 | 8.42 | 2.54 | N/S | N/S | N/S | N/S | <0.005 | 0.02 | 0.002 | 0.095 | <0.002 | 0.01 | 0.249 | 3.25 | 0.21 | 0.007 | 0.101 | N/S | 0.015 | <0.004 | <0.004 | 1.534 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-07-06 | 7.5 | N/S | N/S | 784 | 190 | 13 | 4.4 | 4.22 | 3.27 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-07 | 7.6 | N/S | N/S | 816 | 122 | 12 | 6.4 | 4.9 | 4.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-08 | 7.6 | N/S | N/S | 776 | 116 | 12 | 7.4 | 6.78 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-09 | 7.7 | N/S | N/S | 826 | 168 | 16 | 9.6 | 6.18 | 4.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-10 | 7.4 | 126 | 63 | 870 | 240 | 23 | 9.3 | 5.25 | 5.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2022-07-11 | 7.4 | 85 | 41 | 774 | 172 | 20 | 9.8 | 4.02 | 4.91 | N/S | 154.19 | 0.6 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 59
2022-07-12 | 7.4 | N/S | N/S | 772 | 142 | 17 | 8.7 | 6.44 | 4.67 | 3.06 | N/S | N/S | N/S | N/S | T/X | T/X | <0.002 | 0.037 | <0.002 | <0.004 | 0.042 | 0.66 | 0.11 | <0.002 | 0.068 | N/S | 0.005 | <0.004 | <0.004 | 0.747 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-07-13 | 7.5 | N/S | N/S | 778 | 122 | 26 | 16.4 | 5.22 | 5.74 | N/S | N/S | N/S | N/S | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-14 | 7 | N/S | N/S | 774 | 134 | 28 | 17.7 | 4.26 | 6.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-15 | 6.9 | N/S | N/S | 906 | 280 | 16 | 10.5 | 5.19 | 4.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-16 | 7.3 | N/S | N/S | 358 | 132 | 13 | 8.8 | 5.15 | 3.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-17 | 7.3 | 64 | 30 | 778 | 126 | 17 | 9.3 | 4.31 | 4.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 49
2022-07-18 | 7.3 | 63 | 29 | 788 | 58 | 18 | 10.7 | 4.09 | 4.67 | N/S | 151.6 | 0.6 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 49
2022-07-19 | 7.4 | N/S | N/S | 708 | 72 | 17 | 10.5 | 4.06 | 4.49 | 3.49 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.032 | <0.002 | <0.004 | 0.028 | 0.47 | 0.14 | <0.002 | 0.06 | N/S | 0.004 | <0.004 | <0.004 | 0.659 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-07-20 | 7.3 | N/S | N/S | 728 | 108 | 19 | 10.8 | 3.76 | 4.99 | N/S | N/S | N/S | N/S | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-21 | 7.3 | N/S | N/S | 720 | 114 | 17 | 10.3 | 4.12 | 5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-22 | 7.2 | N/S | N/S | 758 | 136 | 15 | 9.6 | 4.17 | 4.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-23 | 7.2 | N/S | N/S | 1002 | 464 | 9 | 5 | 1.95 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-24 | 7.6 | 106 | 52 | 756 | 184 | 14 | 5.2 | 4.51 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 68
2022-07-25 | 7.6 | 50 | 22 | 756 | 80 | 12 | 6.1 | 5.6 | 3.07 | N/S | 152.83 | 0.5 | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 42
2022-07-26 | 7.4 | N/S | N/S | 782 | 106 | 15 | 8.6 | 4.4 | 3.44 | 2.15 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.038 | <0.002 | <0.004 | 0.031 | 0.52 | 0.12 | <0.002 | 0.052 | N/S | 0.006 | <0.004 | <0.004 | 0.757 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-07-27 | 7.2 | N/S | N/S | 720 | 92 | 15 | 8.8 | 3.76 | 4.35 | N/S | N/S | N/S | N/S | 9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-28 | 7.5 | N/S | N/S | 802 | 138 | 17 | 9.2 | 5.87 | 4.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-29 | 7.4 | N/S | N/S | 696 | 82 | 14 | 8.8 | 5.51 | 4.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-30 | 7.3 | N/S | N/S | 696 | 85 | 15 | 9.6 | 4.08 | 4.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-07-31 | 7.2 | 89 | 43 | 750 | 200 | 19 | 10.2 | 3.66 | 4.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2022-08-01 | 7.3 | 145 | 74 | 848 | 163 | 20 | 10.3 | 3.62 | 5.46 | N/S | 148.82 | 0.6 | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 83
2022-08-02 | 7.3 | N/S | N/S | 766 | 83 | 16 | 9.4 | 4.38 | 5.1 | 4.07 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.032 | <0.002 | <0.004 | 0.027 | 0.47 | 0.12 | <0.002 | 0.05 | N/S | 0.005 | <0.004 | <0.004 | 0.614 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-08-03 | 7.3 | N/S | N/S | 754 | 137 | 21 | 12.1 | 3.63 | 5.89 | N/S | N/S | N/S | N/S | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-04 | 7.3 | N/S | N/S | 732 | 87 | 18 | 11.4 | 3.79 | 5.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-05 | 7.3 | N/S | N/S | 740 | 152 | 15 | 9.5 | 5.54 | 4.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-06 | 7.2 | N/S | N/S | 788 | 224 | 16 | 9.2 | 4.89 | 4.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-07 | 7.2 | 499 | 289 | 958 | 470 | 24 | 7 | 2.6 | 5.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 182
2022-08-08 | 7.5 | 137 | 69 | 768 | 186 | 14 | 5.1 | 4.87 | 3.42 | N/S | 126.61 | 0.5 | 60 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 80
2022-08-09 | 7.5 | N/S | N/S | 778 | 130 | 14 | 6.1 | 8.79 | 3.64 | 2.09 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.043 | <0.002 | <0.004 | 0.035 | 0.46 | 0.07 | <0.002 | 0.048 | N/S | 0.004 | <0.004 | <0.004 | 0.791 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-08-10 | 7.4 | N/S | N/S | 862 | 240 | 20 | 7.9 | 4.39 | 4.62 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-11 | 7.3 | N/S | N/S | 744 | 96 | 16 | 9.9 | 4.87 | 4.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-12 | 7.4 | N/S | N/S | 718 | 84 | 13 | 9.3 | 5.28 | 3.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-13 | 7.3 | N/S | N/S | 808 | 172 | 14 | 9.9 | 6.26 | 4.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-14 | 7.3 | 85 | 41 | 754 | 116 | 17 | 9.6 | 6.58 | 4.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 59
2022-08-15 | 7.3 | T/X | T/X | 760 | 106 | 17 | 9.9 | 6.39 | 4.09 | N/S | 150.27 | 0.6 | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | T/X
2022-08-16 | 7.3 | N/S | N/S | 742 | 106 | 18 | 10.2 | 5.78 | 5.25 | 3.84 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.038 | <0.002 | <0.004 | 0.041 | 0.67 | 0.14 | <0.002 | 0.056 | N/S | 0.005 | <0.004 | <0.004 | 0.766 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-08-17 | 7.3 | N/S | N/S | 746 | 96 | 18 | 11.1 | 5.09 | 5.8 | N/S | N/S | N/S | N/S | 42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-18 | 7.2 | N/S | N/S | 686 | 96 | 19 | 12.4 | 4.36 | 5.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-19 | 7.1 | N/S | N/S | 806 | 186 | 18 | 13.1 | 4.08 | 5.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-20 | 7.2 | N/S | N/S | 1082 | 512 | 13 | 8.2 | 4.1 | 3.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-21 | 7.2 | 98 | 48 | 766 | 144 | 14 | 7.1 | 5.05 | 3.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 64
2022-08-22 | 7.2 | 58 | 27 | 690 | 72 | 14 | 8.6 | 4.79 | 4.05 | N/S | 145.33 | 0.6 | 45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 46
2022-08-23 | 7.2 | N/S | N/S | 802 | 98 | 16 | 9.3 | 4.9 | 4.69 | 3.57 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.033 | <0.002 | <0.004 | 0.037 | 0.59 | 0.12 | <0.002 | 0.057 | N/S | 0.004 | <0.004 | <0.004 | 0.863 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-08-24 | 7.2 | N/S | N/S | 714 | 94 | 20 | 12.8 | 3.98 | 4.92 | N/S | N/S | N/S | N/S | 38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-25 | 7.2 | N/S | N/S | 890 | 212 | 20 | 10 | 3.91 | 5.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-26 | 7.3 | N/S | N/S | 720 | 124 | 12 | 8.3 | 7.13 | 4.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-27 | 7.2 | N/S | N/S | 722 | 112 | 22 | 9 | 6.81 | 5.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-08-28 | 7.1 | 262 | 141 | 880 | 264 | 21 | 9.7 | 5.36 | 5.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 121
2022-08-29 | 7.1 | 161 | 83 | 794 | 260 | 14 | 5.3 | 3.4 | 3.27 | N/S | 118.75 | 0.5 | 53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 88
2022-08-30 | 7.4 | N/S | N/S | 676 | 88 | 14 | 8.7 | 3.94 | 3.16 | 2.34 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.033 | <0.002 | <0.004 | 0.028 | 0.74 | 0.09 | <0.002 | 0.046 | N/S | 0.004 | <0.004 | <0.004 | 0.754 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-08-31 | 7.4 | N/S | N/S | 688 | 87 | 14 | 8.9 | 4.78 | 3.85 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-01 | 7.4 | N/S | N/S | 788 | 132 | 16 | 8.4 | 7.64 | 4.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-02 | 7.3 | N/S | N/S | 758 | 98 | 10 | 7.2 | 8.36 | 4.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-03 | 7.3 | N/S | N/S | 722 | 100 | 15 | 10.7 | 5.11 | 4.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-04 | 7.2 | 31 | 13 | 702 | 68 | 16 | 10.2 | 4.87 | 4.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 31
2022-09-05 | 7.3 | 60 | 28 | 714 | 80 | 16 | 10.2 | 3.9 | 4.83 | N/S | 133.54 | 0.6 | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 47
2022-09-06 | 7.2 | N/S | N/S | 712 | 108 | 17 | 10.4 | 4.77 | 5.25 | 4.05 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.032 | <0.002 | <0.004 | 0.03 | 0.5 | 0.12 | <0.002 | 0.051 | N/S | 0.003 | <0.004 | <0.004 | 0.857 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-09-07 | 7.2 | N/S | N/S | 782 | 162 | 16 | 8 | 7.81 | 5.15 | N/S | N/S | N/S | N/S | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-08 | 7.2 | N/S | N/S | 716 | 96 | 15 | 8.9 | 9.13 | 4.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-09 | 7.2 | N/S | N/S | 750 | 138 | 17 | 10.4 | 8.43 | 5.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-10 | 7.2 | N/S | N/S | 746 | 170 | 31 | 25.3 | 1.21 | 5.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-11 | 7.1 | 578 | 341 | 1032 | 428 | 38 | 19.5 | 0.51 | 7.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 200
2022-09-12 | 7.6 | 100 | 49 | 648 | 130 | 18 | 11 | 1.17 | 2.83 | N/S | 107.91 | 0.5 | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 65
2022-09-13 | 7.5 | N/S | N/S | 730 | 112 | 12 | 6.6 | 6.83 | 2.82 | 1.63 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.036 | <0.002 | <0.004 | 0.029 | 0.57 | 0.07 | <0.002 | 0.055 | N/S | 0.003 | <0.004 | <0.004 | 1.471 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-09-14 | 7.4 | N/S | N/S | 714 | 82 | 16 | 10.4 | 5.23 | 3.33 | N/S | N/S | N/S | N/S | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-15 | 7.4 | N/S | N/S | 1014 | 298 | 25 | 11 | 4.32 | 4.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-16 | 7.2 | N/S | N/S | 734 | 122 | 16 | 12.8 | 3.81 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-17 | 7.2 | N/S | N/S | 732 | 146 | 15 | 10.4 | 3.21 | 4.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-18 | 7.2 | 92 | 44 | 754 | 164 | 20 | 11.8 | 3.16 | 5.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 62
2022-09-19 | 7.4 | 253 | 136 | 916 | 312 | 20 | 8.5 | 2.1 | 4.84 | N/S | 119.27 | 0.5 | 79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 118
2022-09-20 | 7.4 | N/S | N/S | 672 | 92 | 15 | 8.9 | 3.54 | 4.36 | 3.38 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.035 | <0.002 | <0.004 | 0.028 | 0.5 | 0.1 | <0.002 | 0.044 | N/S | 0.003 | <0.004 | <0.004 | 0.896 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-09-21 | 7.4 | N/S | N/S | 668 | 108 | 13 | 6.5 | 5.74 | 3.75 | N/S | N/S | N/S | N/S | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-22 | 7.4 | N/S | N/S | 660 | 57 | 14 | 9.6 | 5.18 | 4.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-23 | 7.4 | N/S | N/S | 650 | 57 | 14 | 11.6 | 4.19 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-24 | 7.3 | N/S | N/S | 696 | 94 | 19 | 11.8 | 5.8 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-25 | 7.3 | 51 | 23 | 656 | 79 | 16 | 10.9 | 4.32 | 2.84 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 42
2022-09-26 | 7.3 | 49 | 22 | 656 | 78 | 18 | 11.9 | 3.93 | 3.09 | N/S | 132.46 | 0.5 | 40 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 42
2022-09-27 | 7.3 | N/S | N/S | 642 | 78 | 18 | 11.9 | 4.15 | 3.31 | 2.33 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.032 | <0.002 | <0.004 | 0.024 | 0.43 | T/X | <0.002 | 0.046 | N/S | 0.004 | <0.004 | <0.004 | 0.768 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-09-28 | 7.3 | N/S | N/S | 658 | 66 | 18 | 11.6 | 3.93 | 3.52 | N/S | N/S | N/S | N/S | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-29 | 7.2 | N/S | N/S | 808 | 134 | 42 | 21.1 | 3.06 | 6.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-09-30 | 7.2 | N/S | N/S | 674 | 96 | 27 | 15.9 | 3.45 | 4.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-01 | 7.1 | N/S | N/S | 662 | 76 | 21 | 15.8 | 2.71 | 2.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-02 | 7.2 | 102 | 50 | 686 | 98 | 27 | 17.8 | 1.98 | 4.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 66
2022-10-03 | 7.1 | 163 | 84 | 736 | 129 | 32 | 18.3 | 2.58 | 5.08 | N/S | 130.11 | 0.7 | 49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 89
2022-10-04 | 7.1 | N/S | N/S | 740 | 134 | 31 | 17.5 | 3.32 | 4.76 | 2.7 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.037 | <0.002 | <0.004 | 0.037 | 0.58 | 0.13 | <0.002 | 0.071 | N/S | 0.009 | <0.004 | <0.004 | 1.004 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-10-05 | 7.1 | N/S | N/S | 834 | 248 | 35 | 16.7 | 2.17 | 5.08 | N/S | N/S | N/S | N/S | 50 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-06 | 7.1 | N/S | N/S | 876 | 228 | 33 | 17 | 2.21 | 6.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-07 | 7.2 | N/S | N/S | 830 | 224 | 35 | 19.4 | 3.44 | 7.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-08 | 7.1 | N/S | N/S | 822 | 204 | 32 | 20.5 | 5.53 | 5.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-09 | 6.9 | 147 | 75 | 748 | 154 | 34 | 19.3 | 4.08 | 6.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2022-10-10 | 7.1 | 157 | 80 | 772 | 152 | 29 | 16.8 | 2.65 | 5.87 | N/S | 127.28 | 0.7 | 53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 87
2022-10-11 | 7.1 | N/S | N/S | 738 | 168 | 28 | 19 | 2.61 | 6.06 | 4 | N/S | N/S | N/S | N/S | <0.005 | 0.008 | <0.002 | 0.05 | <0.002 | <0.004 | 0.065 | 0.96 | 0.14 | <0.002 | 0.083 | N/S | 0.01 | <0.004 | <0.004 | 0.766 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-10-12 | 7.2 | N/S | N/S | 720 | 178 | 24 | 14.2 | 2.22 | 4.74 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-13 | 7.3 | N/S | N/S | 772 | 194 | 44 | 18 | 3.17 | 7.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-14 | 7.2 | N/S | N/S | 728 | 156 | 27 | 16.8 | 4.53 | 5.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-15 | 7.2 | N/S | N/S | 700 | 146 | 24 | 17.2 | 4.3 | 4.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-16 | 7.1 | 150 | 76 | 738 | 166 | 30 | 16.5 | 3.54 | 5.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 85
2022-10-17 | 7.2 | 129 | 65 | 686 | 104 | 28 | 17.5 | 2.46 | 4.92 | N/S | 124.97 | 0.7 | 24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 77
2022-10-18 | 7.2 | N/S | N/S | 682 | 96 | 29 | 19.8 | 3.02 | 5.26 | 3.81 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.033 | <0.002 | <0.004 | 0.045 | 0.68 | 0.13 | <0.002 | 0.054 | N/S | 0.005 | <0.004 | <0.004 | 0.526 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-10-19 | 7.2 | N/S | N/S | 686 | 108 | 35 | 24.2 | 0.5 | 6.36 | N/S | N/S | N/S | N/S | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-20 | 7.1 | N/S | N/S | 730 | 128 | 33 | 22.7 | 1.09 | 6.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-21 | 7.1 | N/S | N/S | 752 | 168 | 28 | 21.3 | 1.18 | 4.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-22 | 7 | N/S | N/S | 748 | 162 | 25 | 18.7 | 0.35 | 4.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-23 | 6.9 | 187 | 98 | 932 | 350 | 47 | 25.2 | <0.250 | 8.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 97
2022-10-24 | 7 | 248 | 133 | 886 | 317 | 36 | 21.5 | <0.250 | 7.31 | N/S | 124.13 | 0.7 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 117
2022-10-25 | 6.8 | N/S | N/S | 1404 | 828 | 52 | 21.7 | <0.250 | 9.24 | 4.39 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.084 | <0.002 | 0.008 | 0.168 | 2.46 | 0.19 | 0.005 | 0.104 | N/S | 0.011 | <0.004 | <0.004 | 0.724 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-10-26 | 7.3 | N/S | N/S | 778 | 212 | 38 | 18.5 | 0.94 | 6.26 | N/S | N/S | N/S | N/S | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-27 | 7.3 | N/S | N/S | 714 | 138 | 30 | 19.3 | 1.94 | 4.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-28 | 7.3 | N/S | N/S | 766 | 194 | 29 | 20 | 2.92 | 4.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-29 | 7.1 | N/S | N/S | 706 | 126 | 28 | 19.1 | 2.77 | 4.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-10-30 | 7.1 | 85 | 41 | 704 | 132 | 28 | 18.9 | 2.08 | 5.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 59
2022-10-31 | 7.2 | 78 | 37 | 652 | 89 | 25 | 17.8 | 1.71 | 4.68 | N/S | 128.55 | 0.6 | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 56
2022-11-01 | 7.1 | N/S | N/S | 726 | 114 | 33 | 20.3 | 2.29 | 5.46 | 3.26 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.032 | <0.002 | <0.004 | 0.039 | 0.55 | 0.13 | <0.002 | 0.061 | N/S | 0.004 | <0.004 | <0.004 | 0.526 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-11-02 | 7.1 | N/S | N/S | 722 | 116 | 32 | 18.7 | 2.86 | 5.51 | N/S | N/S | N/S | N/S | 49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-03 | 7 | N/S | N/S | 664 | 108 | 28 | 19 | 2.02 | 5.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-04 | 7 | N/S | N/S | 716 | 154 | 25 | 20.7 | 1.79 | 4.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-05 | 7 | N/S | N/S | 720 | 180 | 35 | 22.5 | 0.83 | 5.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-06 | 7.3 | 169 | 87 | 768 | 226 | 32 | 18.6 | 3.46 | 6.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 91
2022-11-07 | 7 | 168 | 87 | 770 | 184 | 36 | 18.6 | 2.33 | 6.06 | N/S | 128.36 | 0.6 | 24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 91
2022-11-08 | 7.2 | N/S | N/S | 728 | 130 | 30 | 18.4 | 3.49 | 5.17 | 3.41 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.037 | <0.002 | <0.004 | 0.062 | 0.8 | 0.12 | <0.002 | 0.07 | N/S | 0.009 | <0.004 | <0.004 | 0.545 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-11-09 | 7.1 | N/S | N/S | 678 | 94 | 26 | 17.3 | 2.35 | 4.15 | N/S | N/S | N/S | N/S | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-10 | 7.2 | N/S | N/S | 670 | 122 | 28 | 19.8 | 2.28 | 5.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-11 | 7.1 | N/S | N/S | 826 | 196 | 37 | 23.6 | 3 | 6.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-12 | 7 | N/S | N/S | 700 | 116 | 35 | 22.9 | 1.98 | 5.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-13 | 7.1 | 89 | 43 | 670 | 100 | 26 | 16.3 | 4.62 | 5.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2022-11-14 | 7.1 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | 22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | S/X
2022-11-15 | 7.1 | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | <0.005 | <0.005 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | <3 | N/S
2022-11-16 | 7.2 | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | 39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-17 | 7.1 | 113 | 56 | 740 | 122 | 30 | 17.1 | 1.8 | 4.72 | 3.14 | 149.57 | 0.7 | N/S | N/S | N/S | N/S | <0.002 | 0.038 | <0.002 | <0.004 | 0.041 | 0.62 | 0.09 | <0.002 | 0.058 | <0.5 | 0.005 | <0.004 | <0.004 | 0.568 | <0.002 | <0.002 | <0.002 | N/S | 71
2022-11-18 | 7.2 | N/S | N/S | 698 | 94 | 25 | 17.2 | 2.07 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-19 | 7.1 | N/S | N/S | 676 | 90 | 24 | 18.1 | 2.15 | 3.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-20 | 6.9 | 105 | 51 | 692 | 116 | 25 | 17 | 2 | 4.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 67
2022-11-21 | 7.3 | 118 | 58 | 704 | 108 | 32 | 19.6 | 1.79 | 4.83 | N/S | 132.13 | 0.7 | 22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 72
2022-11-22 | 7.1 | N/S | N/S | 754 | 168 | 32 | 19.4 | 2.27 | 5.07 | 3.17 | N/S | N/S | N/S | N/S | <0.005 | 0.007 | <0.002 | 0.037 | <0.002 | <0.004 | 0.047 | 0.72 | 0.13 | <0.002 | 0.06 | N/S | 0.009 | <0.004 | <0.004 | 0.677 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-11-23 | 7.1 | N/S | N/S | 680 | 134 | 30 | 18.5 | 4.09 | 5.35 | N/S | N/S | N/S | N/S | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-24 | 7.1 | N/S | N/S | 686 | 142 | 29 | 17.6 | 2.29 | 5.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-25 | 6.8 | N/S | N/S | 700 | 136 | 24 | 17.8 | 2.2 | 4.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-26 | 6.7 | N/S | N/S | 732 | 124 | 27 | 19.4 | 2.07 | 4.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-11-27 | 6.9 | 95 | 46 | 736 | 170 | 31 | 16.3 | 1.8 | 5.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 63
2022-11-28 | 7 | 82 | 39 | 824 | 130 | 26 | 17.1 | 1.72 | 4.85 | N/S | 129.91 | 0.6 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 57
2022-11-29 | 7 | N/S | N/S | 778 | 216 | 31 | 18.5 | 1.75 | 5.93 | 3.78 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.044 | <0.002 | <0.004 | 0.063 | 0.77 | 0.16 | <0.002 | 0.07 | N/S | 0.007 | <0.004 | <0.004 | 0.74 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-11-30 | 7.1 | N/S | N/S | 1454 | 821 | 57 | 20.7 | 2.48 | 9.13 | N/S | N/S | N/S | N/S | 48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-01 | 7.4 | N/S | N/S | 648 | 82 | 27 | 18.1 | 2.94 | 4.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-02 | 7.2 | N/S | N/S | 648 | 74 | 25 | 19 | 2.33 | 3.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-03 | 7.1 | N/S | N/S | 704 | 78 | 24 | 18.9 | 2.62 | 4.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-04 | 7.2 | 65 | 30 | 648 | 94 | 25 | 19.8 | 2.14 | 4.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 50
2022-12-05 | 7.3 | 49 | 22 | 634 | 86 | 27 | 17.8 | 1.96 | 5 | N/S | 119.8 | 0.6 | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 42
2022-12-06 | 7 | N/S | N/S | 964 | 232 | 37 | 19.9 | 4.36 | 7.39 | 3.51 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.057 | <0.002 | <0.004 | 0.095 | 1.41 | 0.1 | <0.002 | 0.078 | N/S | 0.008 | <0.004 | <0.004 | 4.61 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-12-07 | 7.1 | N/S | N/S | 692 | 140 | 30 | 18.9 | 3.93 | 5.74 | N/S | N/S | N/S | N/S | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-08 | 7.2 | N/S | N/S | 706 | 150 | 29 | 19.2 | 3.79 | 5.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-09 | 6.9 | N/S | N/S | 1104 | 496 | 26 | 17.5 | 3.12 | 5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-10 | 7.2 | N/S | N/S | 722 | 106 | 20 | 15.2 | 2.59 | 3.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-11 | 7.1 | 58 | 27 | 714 | 112 | 23 | 15.7 | 2.28 | 3.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 46
2022-12-12 | 7.1 | 113 | 56 | 800 | 174 | 29 | 17.2 | 2.01 | 4.86 | N/S | 145.29 | 0.6 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 71
2022-12-13 | 7.2 | N/S | N/S | 840 | 200 | 30 | 18.3 | 2.19 | 5.41 | 3.52 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.038 | <0.002 | <0.004 | 0.053 | 0.69 | 0.14 | <0.002 | 0.068 | N/S | 0.007 | <0.004 | <0.004 | 0.684 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-12-14 | 7 | N/S | N/S | 848 | 321 | 26 | 14.3 | 1.76 | 4.96 | N/S | N/S | N/S | N/S | 13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-15 | 7.3 | N/S | N/S | 684 | 162 | 13 | 6.8 | 2.01 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-16 | 7.5 | N/S | N/S | 908 | 267 | 15 | 11.3 | 3.07 | 2.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-17 | 7.4 | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-18 | 7.4 | 87 | 42 | 850 | 179 | 25 | 14.9 | 3.05 | 5.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 60
2022-12-19 | 7.3 | 142 | 72 | 796 | 154 | 34 | 20.4 | 1.75 | 6.09 | N/S | 146.46 | 0.6 | 24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 82
2022-12-20 | 7.4 | N/S | N/S | 832 | 150 | 28 | 16.8 | 2.54 | 4.83 | 2.96 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.046 | <0.002 | <0.004 | 0.052 | 0.82 | 0.13 | <0.002 | 0.06 | N/S | 0.007 | <0.004 | <0.004 | 0.562 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-12-21 | 7.3 | N/S | N/S | 728 | 114 | 31 | 19.3 | 1.52 | 4.68 | N/S | N/S | N/S | N/S | 19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-22 | 7.2 | N/S | N/S | 724 | 86 | 25 | 16.3 | 4.5 | 4.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-23 | 7.3 | N/S | N/S | 800 | 140 | 39 | 25.8 | 0.69 | 5.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-24 | 7.4 | N/S | N/S | 880 | 246 | 35 | 21.2 | 1 | 5.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-25 | 7.5 | 76 | 36 | 816 | 106 | 25 | 15.6 | 2.98 | 4.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 55
2022-12-26 | 7.2 | 89 | 43 | 744 | 84 | 26 | 18.3 | 2.43 | 3.88 | N/S | 156.07 | 0.6 | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2022-12-27 | 7.3 | N/S | N/S | 770 | 94 | 26 | 16.9 | 0.8 | 3.97 | 2.54 | N/S | N/S | N/S | N/S | <0.005 | 0.008 | <0.002 | 0.035 | <0.002 | <0.004 | 0.032 | 0.43 | 0.11 | <0.002 | 0.048 | N/S | 0.004 | <0.004 | <0.004 | 0.329 | <0.002 | <0.002 | <0.002 | <3 | N/S
2022-12-28 | 7.3 | N/S | N/S | 790 | 84 | 25 | 19 | 2.47 | 4.12 | N/S | N/S | N/S | N/S | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-29 | 7.2 | N/S | N/S | 880 | 156 | 29 | 19.8 | 2.53 | 4.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-30 | 7.2 | N/S | N/S | 872 | 76 | 35 | 23 | 1.23 | 5.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2022-12-31 | 7.4 | N/S | N/S | 816 | 78 | 25 | 17.3 | 2.14 | 4.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
Reporting Limit |  |  |  | 25 | 2 | 1 | 0.3 | 0.25 | 0.15 | 0.15 | 0.5 | 0.1 | 5 | 5 | 0.005 | 0.005 | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.5 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 5
Observations | 365 | 103 | 103 | 360 | 361 | 358 | 361 | 361 | 358 | 52 | 52 | 52 | 49 | 52 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 103
Minimum | 6.7 | 24 | 10 | 358 | 57 | 9 | 4.4 | <0.25 | 2.02 | 1.41 | 107.91 | 0.4 | 14 | <5 | <0.005 | <0.005 | <0.002 | 0.032 | <0.002 | <0.004 | 0.024 | 0.33 | 0.07 | <0.002 | 0.044 | <0.5 | 0.003 | <0.004 | <0.004 | 0.039 | <0.002 | <0.002 | <0.002 | <3 | 26
Mean | 7.3 | 146 | 76 | 863 | 162 | 24 | 14.6 | <2.84 | 4.76 | 3.07 | 177.07 | 0.6 | 34 | <25 | <0.004 | <0.005 | <0.001 | 0.046 | <0.001 | <0.004 | 0.055 | 0.82 | 0.14 | <0.002 | 0.067 | <0.4 | 0.007 | <0.003 | <0.003 | 0.619 | <0.001 | <0.001 | <0.001 | <2 | 79
Maximum | 7.8 | 911 | 565 | 1908 | 933 | 57 | 27.9 | 9.13 | 9.24 | 4.7 | 421.85 | 0.9 | 79 | 50 | <0.005 | 0.02 | 0.002 | 0.095 | <0.002 | 0.01 | 0.249 | 3.25 | 0.26 | 0.007 | 0.104 | <0.5 | 0.015 | <0.004 | 0.004 | 4.61 | <0.002 | <0.002 | <0.002 | <3 | 267
*Effective 1/1/21, means are no longer calculated using the Reporting Limit value in place of non-detect/<LOQ results and are now calculated by replacing any non-detect/<LOQ results with the Reporting Limit/(SQRT2).
**Effective 8/1/21, BOD5 and CBOD5 calculated from TOC result.
April 11, 2022, FOG, T/X: Duplicate failure.
April 26, 2022, Fe_SOL, T/X: LCS preperation error.
June 22, 23, 30, 2022, TKN, P-TOT, T/X: Thermal preservation compromised.
June 24, 2022, TS, T/X: Duplicate failure.
July 12, 2022, CN-AMEN, CN GRAB, T/X: Method holding time expired due to inoperable instrument.
August 15, 2022, BOD5, CBOD5, TOC, T/X: Thermal preservation compromised due to refrigerator malfunction.
September 27, 2022, Fe SOL, T/X: Precision failure. Insufficient sample to reanalyze.
October 6, 2022, NO2+NO3_N: Sample MS/MSD recovery failed but LCS passed.
October 18, 2022 Fe_SOL: Sample MS recovery failed but LCS passed.
October 24, 30, 2022, NH3-N: Sample MS/MSD recovery failed but LCS passed.
November 1, 2022 Tl: Sample MS recovery failed but LCS passed.
November 8, 13, 17, 2022, NH3-N: Sample MS/MSD recovery failed but LCS passed.
November 14, 2022, BOD5, CBOD5, TS, SS, TKN, NH3-N, NO2+NO3, P-TOT, TOC, S/X: Thermal preservation requirements not met.
November 15, 2022, TS, SS, TKN, NH3-N, NO2+NO3, P-TOT, As, Ba, Cd, Cr_Tot, Cu, Fe_Tot, Pb, Mn, Hg, Ni, Se, Ag, Zn, Sb, Be, Tl S/X: Thermal preservation requirements not met.
November 16, 2022, TS, SS, TKN, NH3-N, NO2+NO3, P-TOT, S/X: Thermal preservation requirements not met.
December 17, 2022, TS, SS, TKN, NH3-N, NO2+NO3, P-TOT, S/X: Sample mislabeled.

## Egan Raw 2023
| pH | BOD5 | CBOD5 | TS | SS | TKN | NH3-N | NO2+NO3 | P-TOT | P-SOL | Cl | F | FOG | Phenol-Man | CN-AMEN | CN (GRAB) | As | Ba | Cd | Cr_Tot | Cu | Fe_Tot | Fe_Sol | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr_+6 | TOC
Date |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | MG/L | mg/L | mg/L | mg/L | ug/L | mg/L |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L
2023-01-01 | 7.3 | 110 | 54 | 876 | 162 | 28 | 16.1 | 2.7 | 5.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2023-01-02 | 7.2 | 162 | 84 | 962 | 212 | 28 | 16.5 | 2.6 | 5.14 | N/S | 208.96 | 0.6 | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 89
2023-01-03 | 7.5 | N/S | N/S | 1118 | 462 | 31 | 12.5 | 2.2 | 5.9 | 2.64 | N/S | N/S | N/S | N/S | <0.005 | 0.0084 | <0.002 | 0.056 | <0.002 | <0.004 | 0.112 | 1.39 | 0.16 | 0.002 | 0.07 | N/S | 0.006 | <0.004 | <0.004 | 0.679 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-01-04 | 7.5 | N/S | N/S | 812 | 118 | 16 | 8.6 | 2.6 | 2.8 | N/S | N/S | N/S | N/S | <5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-05 | 7.5 | N/S | N/S | 816 | 104 | 17 | 10.6 | 2.8 | 3.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-06 | 7.4 | N/S | N/S | 906 | 100 | 21 | 13.6 | 3.5 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-07 | 7.4 | N/S | N/S | 860 | 132 | 22 | 14.6 | 3.2 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-08 | 7.4 | 126 | 63 | 846 | 148 | 25 | 13.3 | 2.7 | 3.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2023-01-09 | 7.4 | 104 | 51 | 842 | 124 | 24 | 15.4 | 3.6 | 4.04 | N/S | 176.08 | 0.6 | 34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 67
2023-01-10 | 7.4 | N/S | N/S | 820 | 106 | 24 | 16.3 | 4 | 4.19 | 2.77 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.037 | <0.002 | <0.004 | 0.042 | 0.59 | 0.12 | <0.002 | 0.059 | N/S | 0.004 | <0.004 | <0.004 | 0.517 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-01-11 | 7.3 | N/S | N/S | 794 | 88 | 23 | 16.5 | 3.4 | 4.3 | N/S | N/S | N/S | N/S | 23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-12 | 7.3 | N/S | N/S | 852 | 138 | 27 | 16.5 | 4.2 | 5.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-13 | 7.3 | N/S | N/S | 806 | 114 | 27 | 17.3 | 2.6 | 4.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-14 | 7.3 | N/S | N/S | 792 | 138 | 23 | 15.6 | 3 | 3.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-15 | 7.3 | 102 | 50 | 790 | 132 | 26 | 16.8 | 3.3 | 4.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 66
2023-01-16 | 7.2 | 146 | 74 | 900 | 216 | 30 | 18 | 2.8 | 5.66 | N/S | 157.03 | 0.6 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 83
2023-01-17 | 7.3 | N/S | N/S | 816 | 120 | 24 | 15.2 | 3.4 | 4.04 | 2.69 | N/S | N/S | N/S | N/S | <0.005 | 0.0051 | <0.002 | 0.037 | <0.002 | <0.004 | 0.042 | 0.56 | 0.11 | <0.002 | 0.066 | N/S | 0.006 | <0.004 | <0.004 | 0.443 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-01-18 | 7.3 | N/S | N/S | 920 | 232 | 29 | 18 | 4.1 | 5.28 | N/S | N/S | N/S | N/S | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-19 | 7.4 | N/S | N/S | 940 | 284 | 26 | 12.9 | 3 | 4.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-20 | 7.4 | N/S | N/S | 814 | 102 | 24 | 12.7 | 2.9 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-21 | 7.4 | N/S | N/S | 828 | 122 | 19 | 11.3 | 3.4 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-22 | 7.3 | 65 | 30 | 800 | 84 | 23 | 12.8 | 2.4 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 50
2023-01-23 | 7.3 | 111 | 55 | 882 | 120 | 26 | 14.7 | 2.8 | 4.08 | N/S | 207.36 | 0.5 | 22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2023-01-24 | 7.3 | N/S | N/S | 902 | 164 | 29 | 16.2 | 3.9 | 4.24 | 2.7 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.034 | <0.002 | <0.004 | 0.046 | 0.6 | 0.11 | <0.002 | 0.064 | N/S | 0.005 | <0.004 | <0.004 | 0.45 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-01-25 | 7.3 | N/S | N/S | 958 | 168 | 26 | 15.8 | 4.2 | 4.76 | N/S | N/S | N/S | N/S | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-26 | 7.3 | N/S | N/S | 1036 | 148 | 24 | 15.1 | 3.9 | 4.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-27 | 7.3 | N/S | N/S | 1032 | 130 | 25 | 15.5 | 3.6 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-28 | 7.3 | N/S | N/S | 1034 | 152 | 24 | 16.6 | 4.1 | 3.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-01-29 | 7.1 | 245 | 131 | 1066 | 326 | 31 | 17.3 | 3 | 5.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 116
2023-01-30 | 7.4 | 160 | 82 | 1008 | 144 | 30 | 18.9 | 3.7 | 5.31 | N/S | 269.36 | 0.6 | 37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 88
2023-01-31 | 7.4 | N/S | N/S | 962 | 146 | 33 | 21.6 | 1.7 | 5.69 | 3.64 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.05 | <0.002 | <0.004 | 0.053 | 0.74 | 0.17 | <0.002 | 0.077 | N/S | 0.007 | <0.004 | <0.004 | 0.244 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-02-01 | 7.4 | N/S | N/S | 928 | 182 | 33 | 19.5 | 1.9 | 5.9 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-02 | 7.3 | N/S | N/S | 844 | 146 | 31 | 17.1 | 3.9 | 5.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-03 | 7.1 | N/S | N/S | 1120 | 352 | 27 | 18.2 | 1 | 5.53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-04 | 7.3 | N/S | N/S | 880 | 174 | 29 | 22.2 | 1.8 | 4.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-05 | 7.3 | 205 | 108 | 870 | 180 | 33 | 18.7 | 1.7 | 5.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 103
2023-02-06 | 7.3 | 219 | 116 | 904 | 198 | 32 | 18.9 | 1.3 | 5.56 | N/S | 198.37 | 0.6 | 45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2023-02-07 | 7.2 | N/S | N/S | 932 | 142 | 29 | 17.4 | 0.9 | 4.85 | 3.23 | N/S | N/S | N/S | N/S | <0.005 | 0.0053 | <0.002 | 0.055 | <0.002 | <0.004 | 0.054 | 0.81 | 0.2 | <0.002 | 0.074 | N/S | 0.005 | <0.004 | <0.004 | 0.123 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-02-08 | 7.4 | N/S | N/S | 1158 | 328 | 32 | 17 | 0.8 | 5.37 | N/S | N/S | N/S | N/S | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-09 | 7.2 | N/S | N/S | 1390 | 516 | 38 | 14.5 | 1.1 | 6.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-10 | 7.6 | N/S | N/S | 1020 | 144 | 18 | 10.1 | 2.1 | 2.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-11 | 7.5 | N/S | N/S | 1050 | 184 | 20 | 11.9 | 2 | 3.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-12 | 7.7 | 130 | 65 | 1020 | 120 | 25 | 16.1 | <0.5 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 77
2023-02-13 | 7.5 | 149 | 76 | 1028 | 154 | 27 | 16.5 | <0.5 | 4.23 | N/S | 241.43 | 0.5 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2023-02-14 | 7.5 | N/S | N/S | 942 | 116 | 27 | 17.3 | 0.7 | 3.85 | 2.35 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.052 | <0.002 | <0.004 | 0.05 | 0.75 | 0.27 | <0.002 | 0.066 | N/S | 0.004 | <0.004 | <0.004 | 0.079 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-02-15 | 7.2 | N/S | N/S | 974 | 172 | 28 | 15.5 | 0.8 | 4.33 | N/S | N/S | N/S | N/S | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-16 | 7.5 | N/S | N/S | 1002 | 176 | 29 | 15.5 | 1.3 | 4.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-17 | 7.4 | N/S | N/S | 1056 | 96 | 22 | 15.2 | 1.3 | 2.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-18 | 7.7 | N/S | N/S | 1100 | 164 | 24 | 13.5 | 0.7 | 3.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-19 | 7.6 | 113 | 56 | 1150 | 190 | 22 | 14.1 | 1.5 | 3.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 71
2023-02-20 | 7.5 | 127 | 63 | 1124 | 202 | 21 | 12.1 | 1.1 | 3.21 | N/S | 296.8 | 0.5 | 40 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 76
2023-02-21 | 7.4 | N/S | N/S | 1044 | 154 | 25 | 13.7 | 0.8 | 3.82 | 2.3 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.055 | <0.002 | <0.004 | 0.05 | 0.71 | 0.07 | <0.002 | 0.069 | N/S | 0.005 | <0.004 | <0.004 | 1.138 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-02-22 | 7.4 | N/S | N/S | 1128 | 296 | 27 | 12.5 | 0.5 | 4.55 | N/S | N/S | N/S | N/S | 11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-23 | 7.6 | N/S | N/S | 960 | 190 | 16 | 5.4 | 2 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-24 | 7.8 | N/S | N/S | 1014 | 118 | 18 | 8.9 | 1.2 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-25 | 7.8 | N/S | N/S | 968 | 164 | 17 | 11.5 | 1.8 | 1.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-02-26 | 7.4 | 212 | 112 | 1056 | 262 | 27 | 12.4 | 1.2 | 4.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 105
2023-02-27 | 7.5 | 219 | 116 | 1098 | 312 | 29 | 8.8 | 1.9 | 4.67 | N/S | 213.64 | 0.4 | 25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 108
2023-02-28 | 7.6 | N/S | N/S | 1010 | 248 | 23 | 7.9 | 2.1 | 3.69 | 1.11 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.066 | <0.002 | 0.004 | 0.075 | 1.57 | 0.05 | 0.002 | 0.069 | N/S | 0.006 | <0.004 | <0.004 | 1.159 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-03-01 | 7.5 | N/S | N/S | 1120 | 328 | 26 | 9.6 | 1.8 | 5.21 | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-02 | 7.7 | N/S | N/S | 1004 | 174 | 22 | 11.5 | 2 | 3.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-03 | 7.5 | N/S | N/S | 1072 | 388 | 24 | 13.7 | 1.7 | 2.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-04 | 7.6 | N/S | N/S | 854 | 168 | 19 | 13.1 | 2.1 | 2.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-05 | 7.5 | 87 | 42 | 848 | 180 | 24 | 19.3 | 2 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 60
2023-03-06 | 7.4 | 75 | 35 | 852 | 106 | 24 | 12.8 | 1.8 | 3.03 | N/S | 222.97 | 0.5 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 54
2023-03-07 | 7.4 | N/S | N/S | 1266 | 416 | 30 | 14.2 | 1.3 | 4.99 | 1.88 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.063 | <0.002 | <0.004 | 0.069 | 1.26 | 0.1 | <0.002 | 0.08 | N/S | 0.008 | <0.004 | <0.004 | 0.827 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-03-08 | 7.7 | N/S | N/S | 864 | 64 | 21 | 15.2 | 1.7 | 3.24 | N/S | N/S | N/S | N/S | 13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-09 | 7.4 | N/S | N/S | 984 | 232 | 31 | 16.6 | 2.3 | 5.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-10 | 7.5 | N/S | N/S | 1106 | 244 | 21 | 15.6 | 1.8 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-11 | 7.4 | N/S | N/S | 1046 | 176 | 22 | 14 | 2 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-12 | 7.5 | 140 | 71 | 1026 | 221 | 27 | 14.2 | 1.1 | 4.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 81
2023-03-13 | 7.5 | 136 | 69 | 1004 | 184 | 28 | 17 | 2 | 3.72 | N/S | 253.99 | 0.5 | 17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 80
2023-03-14 | 7.7 | N/S | N/S | 962 | 134 | 27 | 14.1 | 1 | 3.16 | 1.76 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.053 | <0.002 | <0.004 | 0.045 | 0.68 | 0.09 | <0.002 | 0.056 | N/S | 0.006 | <0.004 | <0.004 | 0.702 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-03-15 | 7.7 | N/S | N/S | 1002 | 184 | 25 | 12.6 | 2.4 | 3.61 | N/S | N/S | N/S | N/S | 11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-16 | 7.5 | N/S | N/S | 956 | 190 | 28 | 12.8 | 3 | 3.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-17 | 7.5 | N/S | N/S | 886 | 94 | 18 | 10.2 | 1.5 | 2.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-18 | 7.5 | N/S | N/S | 868 | 80 | 19 | 11.2 | 1.2 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-19 | 7.3 | 90 | 44 | 862 | 78 | 24 | 14.5 | 1.1 | 3.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 61
2023-03-20 | 7.6 | 123 | 61 | 1032 | 232 | 29 | 15.9 | 1.7 | 4.83 | N/S | 218.81 | 0.6 | 31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 75
2023-03-21 | 7.5 | N/S | N/S | 1016 | 210 | 28 | 15.8 | 2.3 | 4.83 | 2.53 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.049 | <0.002 | <0.004 | 0.051 | 0.82 | T/X | <0.002 | 0.08 | N/S | 0.009 | <0.004 | <0.004 | 0.689 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-03-22 | 7.3 | N/S | N/S | 1154 | 312 | 32 | 15.6 | 3 | 6.32 | N/S | N/S | N/S | N/S | 18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-23 | 7.4 | N/S | N/S | 960 | 212 | 29 | 14.2 | 2.7 | 5.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-24 | 7.4 | N/S | N/S | 1124 | 374 | 21 | 15 | 2.2 | 3.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-25 | 7.5 | N/S | N/S | 974 | 337 | 16 | 8.8 | 1.8 | 2.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-26 | 7.6 | 118 | 59 | 1026 | 248 | 21 | 8.1 | 1.9 | 3.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 73
2023-03-27 | 7.7 | 67 | 31 | 910 | 152 | 21 | 9.1 | 2 | 3.61 | N/S | 214.71 | 0.4 | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 50
2023-03-28 | 7.6 | N/S | N/S | 972 | 184 | 23 | 11.1 | 1.8 | 4.36 | 2.07 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.061 | <0.002 | <0.004 | 0.057 | 1.25 | 0.07 | <0.002 | 0.089 | N/S | 0.008 | <0.004 | <0.004 | 0.973 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-03-29 | 7.6 | N/S | N/S | 1040 | 252 | 32 | 12.5 | 2.2 | 5.81 | N/S | N/S | N/S | N/S | 11 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-30 | 7.5 | N/S | N/S | 1026 | 256 | 40 | 13.8 | 2.2 | 6.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-03-31 | 7.4 | N/S | N/S | 1180 | 508 | 28 | 11 | 3.4 | 5.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-01 | 7.6 | N/S | N/S | 848 | 216 | 17 | 6.2 | 3.25 | 3.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-02 | 7.6 | 117 | 58 | 982 | 308 | 22 | 7.9 | 2.75 | 4.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 72
2023-04-03 | 7.6 | 101 | 49 | 1034 | 264 | 23 | 9.4 | 2.91 | 4.21 | N/S | 193.87 | 0.5 | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 66
2023-04-04 | 7.6 | N/S | N/S | 820 | 214 | 20 | 6.9 | 2.97 | 3.48 | 1.37 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.054 | <0.002 | <0.004 | 0.056 | 1.34 | 0.07 | <0.002 | 0.072 | N/S | 0.006 | <0.004 | <0.004 | 1.05 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-04-05 | 7.5 | N/S | N/S | 656 | 68 | 11 | 5.4 | 2.66 | 1.63 | N/S | N/S | N/S | N/S | <5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-06 | 7.7 | N/S | N/S | 794 | 110 | 15 | 8.5 | 3.21 | 2.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-07 | 7.7 | N/S | N/S | 888 | 132 | 13 | 9.5 | 2.65 | 1.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-08 | 7.7 | N/S | N/S | 990 | 260 | 16 | 10.5 | 2.48 | 2.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-09 | 7.6 | 111 | 55 | 954 | 204 | 26 | 11.6 | 2.15 | 4.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 70
2023-04-10 | 7.4 | 71 | 33 | 912 | 212 | 26 | 11.9 | 2.41 | 4.98 | N/S | 196.37 | 0.6 | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 52
2023-04-11 | 7.4 | N/S | N/S | 924 | 183 | 24 | 10.8 | 2.68 | 4.72 | 2.53 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.052 | <0.002 | <0.004 | 0.05 | 1.07 | 0.09 | <0.002 | 0.08 | N/S | 0.007 | <0.004 | <0.004 | 1.015 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-04-12 | 7.4 | N/S | N/S | 846 | 106 | 20 | 11.8 | 2.82 | 4.04 | N/S | N/S | N/S | N/S | 19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-13 | 7.4 | N/S | N/S | 868 | 156 | 22 | 12.4 | 2.6 | 4.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-14 | 7.5 | N/S | N/S | 914 | 200 | 20 | 11.9 | 2.91 | 4.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-15 | 7.4 | N/S | N/S | 902 | 212 | 17 | 10.7 | 2.75 | 3.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-16 | 7.1 | 372 | 209 | 1332 | 556 | 51 | 13.4 | 2.66 | 9.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 151
2023-04-17 | 7.4 | 183 | 96 | 1000 | 240 | 38 | 15.3 | 3.19 | 6.51 | N/S | 185.18 | 0.6 | 44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 96
2023-04-18 | 7.3 | N/S | N/S | 1030 | 304 | 33 | 15.6 | 4.39 | 6.7 | 3.09 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.065 | <0.002 | <0.004 | 0.082 | 2.22 | 0.1 | 0.003 | 0.104 | N/S | 0.009 | <0.004 | <0.004 | 0.945 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-04-19 | 7.4 | N/S | N/S | 920 | 260 | 30 | 14 | 3.55 | 5.88 | N/S | N/S | N/S | N/S | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-20 | 7.5 | N/S | N/S | 1160 | 480 | 43 | 15.8 | 2.45 | 8.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-21 | 7.5 | N/S | N/S | 848 | 150 | 17 | 14 | 2.93 | 3.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-22 | 7.4 | N/S | N/S | 1074 | 408 | 23 | 15.6 | 2.56 | 4.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-23 | 7.4 | 153 | 78 | 1072 | 320 | 37 | 18.6 | 3.37 | 6.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2023-04-24 | 7.4 | 293 | 160 | 948 | 228 | 35 | 17.3 | 2.41 | 6.51 | N/S | 180.6 | 0.7 | 21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 129
2023-04-25 | 7.4 | N/S | N/S | 976 | 284 | 36 | 16.4 | 2.89 | 7.03 | 3 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.063 | <0.002 | 0.006 | 0.082 | 1.41 | 0.12 | 0.002 | 0.117 | N/S | 0.01 | <0.004 | <0.004 | 0.756 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-04-26 | 7.6 | N/S | N/S | 1018 | 344 | 45 | 21.8 | <0.50 | 8.26 | N/S | N/S | N/S | N/S | 17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-27 | 7.6 | N/S | N/S | 948 | 252 | 45 | 23.3 | <0.50 | 7.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-28 | 7.4 | N/S | N/S | 1242 | 584 | 33 | 15.3 | 4.73 | 7.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-29 | 7.5 | N/S | N/S | 1468 | 753 | 26 | 17.3 | 2.68 | 5.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-04-30 | 7.2 | 456 | 262 | 1476 | 508 | 70 | 16.9 | 2.01 | 14.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 172
2023-05-01 | 7.2 | 804 | 492 | 1304 | 700 | 57 | 16.6 | 2.04 | 11.33 | N/S | 176.95 | 0.6 | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 247
2023-05-02 | 7.6 | N/S | N/S | 1054 | 412 | 40 | 15.5 | 2.29 | 8.77 | 3.28 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.091 | <0.002 | <0.004 | 0.122 | 2.08 | 0.11 | 0.004 | 0.157 | N/S | 0.012 | <0.004 | <0.004 | 1.116 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-05-03 | 7.4 | N/S | N/S | 1254 | 588 | 50 | 15.9 | 2.79 | 11.08 | N/S | N/S | N/S | N/S | 17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-04 | 7.3 | N/S | N/S | 1204 | 516 | 45 | 15.3 | 2.62 | 10.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-05 | 7.3 | N/S | N/S | 1152 | 470 | 22 | 15.6 | 3.01 | 4.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-06 | 7.3 | N/S | N/S | 1178 | 520 | 20 | 15.3 | 3.02 | 4.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-07 | 6.6 | 183 | 96 | 1056 | 427 | 39 | 14.4 | 2.61 | 9.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 96
2023-05-08 | 7.2 | 171 | 88 | 1008 | 336 | 32 | 14.5 | 2.73 | 7.13 | N/S | 163.09 | 0.6 | 43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 92
2023-05-09 | 7.5 | N/S | N/S | 956 | 272 | 32 | 13.5 | 3.14 | 6.9 | 3.69 | N/S | N/S | N/S | N/S | <0.005 | <0.005 | <0.002 | 0.07 | <0.002 | <0.004 | 0.091 | 1.58 | 0.11 | 0.003 | 0.124 | N/S | 0.012 | <0.004 | <0.004 | 1.392 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-05-10 | 7.1 | N/S | N/S | 914 | 236 | 30 | 14.3 | 2.68 | 6.67 | N/S | N/S | N/S | N/S | 14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-11 | 7.2 | N/S | N/S | 1052 | 412 | 36 | 13.2 | 3.17 | 9.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-12 | 7.3 | N/S | N/S | 812 | 176 | 23 | 13.1 | 3.28 | 5.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-13 | 7.4 | N/S | N/S | 744 | 94 | 18 | 11.3 | 3.08 | 4.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-14 | 7.3 | 40 | 18 | 726 | 92 | 18 | 11.9 | 2.97 | 4.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 36
2023-05-15 | 7.3 | 56 | 26 | 728 | 102 | 23 | 13.5 | 3.35 | 5.26 | N/S | 172.81 | 0.6 | 35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 45
2023-05-16 | 7.2 | N/S | N/S | 898 | 248 | 29 | 12.2 | 3.27 | 7.14 | 3.92 | N/S | N/S | N/S | N/S | <0.005 | 0.005 | <0.002 | 0.061 | <0.002 | <0.004 | 0.087 | 1.52 | 0.15 | 0.002 | 0.101 | N/S | 0.017 | <0.004 | <0.004 | 2.676 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-05-17 | 7.2 | N/S | N/S | 966 | 272 | 31 | 11.4 | 3.46 | 7.78 | N/S | N/S | N/S | N/S | 7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-18 | 7.2 | N/S | N/S | 1356 | 740 | 60 | 17.2 | 4.31 | 14.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-19 | 7.1 | N/S | N/S | 1226 | 620 | 23 | 14.1 | 5.12 | 5.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-20 | 7.2 | N/S | N/S | 1162 | 540 | 37 | 13.6 | 4.5 | 8.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-21 | 7 | 153 | 78 | 1256 | 620 | 47 | 15 | 2.96 | 10.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2023-05-22 | 7.3 | 118 | 59 | 860 | 288 | 34 | 14.4 | 3.35 | 8.24 | N/S | 160.11 | 0.6 | 20 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 73
2023-05-23 | 6.5 | N/S | N/S | 1090 | 472 | 41 | 13.4 | 3.27 | 10.85 | 5.17 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.093 | <0.002 | <0.004 | 0.143 | 2.33 | 0.18 | 0.005 | 0.175 | N/S | 0.018 | <0.004 | <0.004 | 2.52 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-05-24 | 7.2 | N/S | N/S | 802 | 128 | 22 | 11.4 | 3.59 | 6.14 | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-25 | 7.4 | N/S | N/S | 722 | 100 | 26 | 14.4 | 4.53 | 6.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-26 | 7.2 | N/S | N/S | 830 | 160 | 48 | 31.6 | 0.74 | 8.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-27 | 7 | N/S | N/S | 1036 | 308 | 32 | 14 | 3.26 | 7.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-05-28 | 7.3 | 47 | 21 | 788 | 140 | 25 | 12.8 | 2.83 | 6.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 40
2023-05-29 | 7.1 | 133 | 67 | 1038 | 360 | 38 | 13.8 | 2.59 | 9.7 | N/S | 155.27 | 0.6 | 16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 78
2023-05-30 | 7.3 | N/S | N/S | 1036 | 308 | 35 | 13.5 | 2.89 | 8.99 | 5.43 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.068 | <0.002 | <0.004 | 0.101 | 1.52 | 0.17 | 0.003 | 0.116 | N/S | 0.01 | <0.004 | <0.004 | 3.391 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-05-31 | 7.2 | N/S | N/S | 1078 | 448 | 43 | 14 | 2.67 | 10.55 | N/S | N/S | N/S | N/S | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-01 | 7.2 | N/S | N/S | 1046 | 416 | 35 | 11.5 | 2.91 | 9.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-02 | 7.4 | N/S | N/S | 978 | 190 | 29 | 13.7 | 3.3 | 8.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-03 | 7.1 | N/S | N/S | 1064 | 320 | 25 | 14.2 | 3.24 | 7.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-04 | 7.1 | 149 | 76 | 1036 | 493 | 49 | 12.9 | 2.83 | 12.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 84
2023-06-05 | 7.2 | 38 | 17 | 978 | 412 | 42 | 13.3 | 2.95 | 11.81 | N/S | 146 | 0.7 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 35
2023-06-06 | 7.1 | N/S | N/S | 1170 | 593 | 47 | 13.5 | 3.09 | 14.2 | 5.98 | N/S | N/S | N/S | N/S | <0.005 | 0.007 | <0.002 | 0.13 | <0.002 | 0.009 | 0.217 | 2.9 | 0.17 | 0.006 | 0.168 | N/S | 0.02 | <0.004 | <0.004 | 5.74 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-06-07 | 7.1 | N/S | N/S | 916 | 325 | 31 | 12.8 | 3.45 | 8.68 | N/S | N/S | N/S | N/S | 36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-08 | 7.2 | N/S | N/S | 894 | 272 | 31 | 14.1 | 3.27 | 8.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-09 | 7.2 | N/S | N/S | 890 | 228 | 20 | 13.7 | 3.3 | 5.76 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-10 | 7 | N/S | N/S | 814 | 200 | 24 | 14.7 | 3.06 | 6.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-11 | 7 | 94 | 45 | 808 | 166 | 26 | 14.8 | 2.66 | 6.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 63
2023-06-12 | 7 | 168 | 86 | 860 | 230 | 30 | 15.5 | 2.57 | 7.18 | N/S | 146.65 | 0.7 | 29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 91
2023-06-13 | 6.9 | N/S | N/S | 1058 | 404 | 37 | 13.9 | 2.24 | 9.29 | 5.36 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.07 | <0.002 | <0.004 | 0.125 | 1.77 | 0.17 | 0.003 | 0.099 | N/S | 0.01 | <0.004 | <0.004 | 0.167 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-06-14 | 7.3 | N/S | N/S | 828 | 252 | 29 | 10.6 | 2.59 | 7.99 | N/S | N/S | N/S | N/S | 30 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-15 | 6.9 | N/S | N/S | 1074 | 440 | 41 | 14.5 | 2.82 | 9.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-16 | 7.1 | N/S | N/S | 808 | 216 | 20 | 13.5 | 3.34 | 5.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-17 | 7.1 | N/S | N/S | 1086 | 464 | 22 | 14.5 | 3.18 | 6.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-18 | 7.2 | 205 | 108 | 992 | 370 | 36 | 14.6 | 2.92 | 9.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 103
2023-06-19 | 7.2 | 122 | 61 | 774 | 184 | 29 | 14.5 | 3.02 | 6.35 | N/S | 138.63 | 0.7 | 28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 74
2023-06-20 | 7.2 | N/S | N/S | 768 | 171 | 28 | 14.1 | 3.03 | 6.54 | 4.02 | N/S | N/S | N/S | N/S | <0.005 | 0.007 | <0.002 | 0.043 | <0.002 | <0.004 | 0.059 | 0.84 | 0.13 | <0.002 | 0.08 | N/S | 0.006 | <0.004 | <0.004 | 4.645 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-06-21 | 7.2 | N/S | N/S | 740 | 155 | 29 | 14.4 | 3.44 | 6.18 | N/S | N/S | N/S | N/S | 52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-22 | 7 | N/S | N/S | 772 | 205 | 29 | 14.2 | 3.51 | 6.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-23 | 7 | N/S | N/S | S/X | S/X | S/X | S/X | S/X | S/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-24 | 6.9 | N/S | N/S | 864 | 272 | T/X | T/X | T/X | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-25 | 6.3 | 155 | 79 | 860 | 276 | 25 | 10.9 | 2.21 | 6.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 86
2023-06-26 | 7.3 | 88 | 42 | 808 | 175 | 21 | 11.5 | 2.66 | 5.48 | N/S | 145.18 | 0.6 | 53 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 60
2023-06-27 | 7.2 | N/S | N/S | 834 | 269 | 29 | 12.5 | 2.92 | 8.31 | 4.83 | N/S | N/S | N/S | N/S | <0.005 | 0.006 | <0.002 | 0.057 | <0.002 | 0.005 | 0.124 | 1.43 | 0.13 | 0.006 | 0.069 | N/S | 0.008 | <0.004 | <0.004 | 5.34 | <0.002 | <0.002 | <0.002 | <3 | N/S
2023-06-28 | 7.1 | N/S | N/S | 838 | 248 | 27 | 13 | 3.07 | 8.48 | N/S | N/S | N/S | N/S | 32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-29 | 6.8 | N/S | N/S | 1314 | 608 | 50 | 13.4 | 2.48 | 12.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2023-06-30 | 7 | N/S | N/S | 1146 | 596 | 20 | 12.7 | 2.85 | 7.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
Reporting Limit |  |  |  | 25 | 2 | 1 | 0.3 | 0.5 | 0.15 | 0.15 | 0.5 | 0.1 | 5 | 5 | 0.005 | 0.005 | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0.01 | 0.01 | 0.001 | 0.001 | 0.5 | 0.001 | 0.002 | 0.002 | 0.005 | 0.001 | 0.001 | 0.001 | 3 | 5
Observations | 181 | 52 | 52 | 180 | 180 | 179 | 179 | 179 | 179 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 52
Minimum | 6.3 | 38 | 17 | 656 | 64 | 11 | 5.4 | <0.50 | 1.63 | 1.11 | 138.63 | 0.4 | 16 | <5 | <0.005 | <0.005 | <0.002 | 0.034 | <0.002 | <0.004 | 0.042 | 0.56 | 0.05 | <0.002 | 0.056 | <0.5 | 0.004 | <0.004 | <0.004 | 0.079 | <0.002 | <0.002 | <0.002 | <3 | 35
Mean | 7.3 | 156 | 82 | 976 | 257 | 28 | 14 | <2.57 | 5.68 | 3.2 | 193.86 | 0.6 | 30 | <19 | <0.004 | <0.005 | <0.001 | 0.061 | <0.001 | <0.003 | 0.08 | 1.3 | 0.13 | <0.002 | 0.092 | <0.4 | 0.009 | <0.003 | <0.003 | 1.491 | <0.001 | <0.001 | <0.001 | <2 | 83
Maximum | 7.8 | 804 | 491 | 1476 | 753 | 70 | 31.6 | 5.12 | 14.88 | 5.98 | 296.8 | 0.7 | 53 | 52 | <0.005 | 0.008 | <0.002 | 0.13 | <0.002 | 0.009 | 0.217 | 2.9 | 0.27 | 0.006 | 0.175 | <0.5 | 0.02 | <0.004 | <0.004 | 5.74 | <0.002 | <0.002 | <0.002 | <3 | 247
*Effective 1/1/21, means are no longer calculated using the Reporting Limit value in place of non-detect/<LOQ results and are now calculated by replacing any non-detect/<LOQ results with the Reporting Limit/(SQRT2).
**Effective 8/1/21, BOD5 and CBOD5 calculated from TOC result.
March 21, 2023, Fe_Sol, T/X: LCS expired.
June 23, 2023, TS, SS, TKN, NH3-N, NO2+NO3, P-TOT, S/X: Thermal preservation not maintained.
June 24, 2023 TKN, NH3-N, NO2+NO3, P-TOT,T/X: Thermal preservation requirements not met.